## Inputs
Inputs |  |  |  |  | Legend
[5 empty] | User input, hard-coded default value | Value
| General Inputs |  |  |  | User input, calculated default value (user can over ride | Value
| Analysis Period (Project Life) | 25 | years (40 max) |  | User input, drop down selection | Value
| Discount Rate | 7% | % per annum |  | Input not applicable (user can over ride) | Value
| Inflation Rate | 2% | % per annum |  | Read-only output | Value
| Desired Confidence that Reserve Covers Cost | 0.92
| Working Hours/year | 2080
Plant Inputs
| Plant Name | Ground Mount Fixed Tilt
| Location | Denver, CO
| Plant Size (kWp DC) | 10000
| Plant Size (Wp DC) | 10000000
| Energy Yield Year 1 (kWh/kWp/year) | 1400
| Plant Installed Cost | 3000000
| Module Efficiency | 16%
| Module Power (W STC) | 305
| Array Area (m2) | 62500
| Number of Modules | 32787
| Module Type/ Degradation | Mono-crystal silicon: 0.36%/year
| Degradation Rate per year | 0.0036
| Modules per String | 14
| Number of Strings | 2341.9204
| Strings per Combiner Box | 15
| Number of Combiner Boxes | 157
| Combiner boxes per DC disconnect | 1
| Number of DC Disconnects | 157
| Inverter Type | Central Inverter
| Inverter Replacement Cost/ Wp | 0.19
| Number of Inverters | 10
| Inverter Capacity (kWp) | 1000
| Number of Transformers | 10
| Inverter Warranty (years) | 10
| PV Module Product Warranty (years) | 20
| Other equipment (EPC) Warranty (years) | 1
| Purchased monitoring contract (years) | 0 | Enter '0' if not applicable
| Market Sector | Utility (1 MW)
| Mounting Location | Ground Mount
| Roof Slope | Sloped, 4:12
| Roof Type | Composite Shingle
| Mounting Type | Attached
| Inspection technique | Arial
| Array Area per Roof Attachment (m2) | 2
| Number of Roof Attachments | 31250
| Ground Coverage Ratio (GCR) | 33%
| Site Area (acres) | 52.62
| Modules/Row | 200
| Total Rows: | 163.9344
| Tracking or Fixed | 1-axis Tracking
| Rows per Tracked Block:(ignore untracked) | 16
| Total Tracking Blocks:(ignore untracked) | 10.2459
| Foundations per row: (ignore rooftop) | 10
Environmental Conditions
Indicate "1" if condition applies to project, "0" if not applicable
| Snow | 0
| Pollen | 0
| Bird Populations | 0 |  | (reduce efficiency 2.67% for central, 0.18% for string inverter, Wang et al 2012)
| Sand/Dust | 0 |  | (reduce efficiency 1%/g, Wang et al 2012)
| Humid | 0
| Hot | 0
| High Wind | 0
| Hail | 0
| Salt Air | 0 |  | (reduce efficiency 1%/g, Wang et al 2012)
| Diesel Soot | 0 |  | (reduce efficiency 1%/g, Wang et al 2012)
| Industrial Emissions | 0
| Construction Site Nearby | 0
| High Insolation | 0 |  | (reduce availability 0.83%, Wang et al 2012)

## Report
Plant Name | Ground Mount Fixed Tilt | Lifetime NPV by Service Provider |  |  |  | Lifetime NPV by O&M Category |  |  |  | Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40
|  | Service Provider | Avg. Cost/Yr | NPV (Life) | % of Total | O&M Category | Avg. Cost/Yr | NPV (Life) | % of Total | Annual Cash Flow | 60724.0436 | 92998.1339 | 93544.6629 | 96139.8825 | 126946.4684 | 100090.6021 | 101371.8554 | 104857.3277 | 106497.7843 | 143417.3473 | 178521.2288 | 180847.5842 | 181165.5114 | 183916.0108 | 223072.7762 | 187584.5878 | 188347.4407 | 191605.664 | 192395.8634 | 238350.6541 | 679236.268 | 685279.8739 | 685970.4451 | 686825.4451 | 729408.8354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Results |  | Administrator | 7717.4876 | 88635.4481 | 4.18% | AC Wiring | 2054.8769 | 22299.464 | 1.052% | Reserve Account Amount | 61847.3281 | 155324.2267 | 150035.0964 | 146930.984 | 172198.2875 | 139985.5371 | 136113.0076 | 135394.4338 | 133363.7579 | 166933.8478 | 271410.4521 | 259362.4633 | 247672.6437 | 240485.5411 | 271424.9643 | 229333.8851 | 226749.2334 | 233371.2664 | 238230.6519 | 287264.2924 | 1519994.1092 | 1492795.7541 | 1444325.0772 | 1382804.7592 | 1351973.4208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annualized O&M Costs ($/year) | 148960.1488 | Cleaner | 23710.3067 | 272344.6707 | 12.85% | DC Wiring | 32954.8097 | 416042.6698 | 19.63%
Annualized Unit O&M Costs ($/kW/year) | 14.896 | Inverter specialist | 29782.305 | 268749.2564 | 12.68% | Asset Management | 4548.8299 | 52249.4118 | 2.465%
Maximum Reserve Account | 1519994.1092 | Inspector | 25548.6409 | 287353.0864 | 13.55% | Documents | 3115.3948 | 35784.488 | 1.688%
Net Present Value O&M Costs (project life) | 2120221.5634 | Journeyman electrician | 11209.7531 | 577876.974 | 27.26% | Electrical | 1795.7882 | 20350.6645 | 0.96%
Net Present Value (project life) per Wp | 0.21202 | PV module/array Specialist | 26303.4526 | 318732.3151 | 15.03% | Mechanical | 5316.9973 | 53304.2233 | 2.515%
NPV Annual O&M Cost per kWh | 0.013451 | Network/IT | 152.4095 | 1530.5846 | 0.07219% | Inverter | 30636.9986 | 277163.5693 | 13.07%
|  | Master electrician | 4790.3476 | 53383.2116 | 2.518% | Meter | 17.8096 | 204.567 | 0.00965%
|  | Mechanic | 2207.3313 | 54081.5864 | 2.551% | Monitoring | 3.4091 | 17.6197 | 0.0008312%
|  | Designer | 0 | 0 | 0% | Roof | 0 | 0 | 0%
|  | Pest control | 1613.7533 | 18536.1204 | 0.8743% | Rack | 105.7134 | 1220.7685 | 0.05759%
|  | Roofing | 0 | 0 | 0% | PV Module | 56090.6538 | 1105116.0864 | 52.13%
|  | Structural engineer | 5.9545 | 69.3909 | 0.003273% | Tracker | 7547.5399 | 86693.618 | 4.09%
|  | Mower/Trimmer | 15573.6644 | 178884.4216 | 8.437% | Transformer | 4395.4969 | 49377.4317 | 2.329%
|  | Utilities locator | 4.365 | 44.4973 | 0.002099% | Whole System | 35.4533 | 396.9814 | 0.01873%
|  | Total | 148619.7715 | 2120221.5634 | 100% | Total | 148584.3182 | 2119824.582 | 100%

## Detailed Measures
Detailed Measures | [23 empty] | Annual Cash Flow |  | Annual Cash Flow | [39 empty] | Reserve Account |  | Reserve Account
Service Description | O&M Type | Service Category | O&M Category | Applicable ? (1= yes, 0 = no) | Covered by Warranty - Materials (1=yes, 0=no) | Covered by Warranty - Labor (1=yes, 0=no) | Warranty or Service Package Type | Applicable Unit | Service Provider | Labor Rate per Hour | Mean Interval (years) | Weibull or Lognormal Shape Factor | Type of Distribution | Approx. Number of Units | Labor hrs per unit | Total Labor Hours/year (not used, just for check) | Material/ Other Cost per unit | Total Labor Cost | Total Matl and Other Cost | Total Cost for Measure | Notes | Reference | Average Annual Expense | NPV (Project Life) | % of Total NPV | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | NPV (Project Life) | % of Total NPV | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40
Insurance Premium | Administration | Management | Asset Management | 1 | 0 | 0 | N/A | percent of initial cost | Administrator | 22.9956 | 1 | 1 | interval | 1 | 0 | 0 | 3000 | 0 | 3000 | 3000 | premium percent of intial cost.04% | David Walters, Hartford Steam Boiler, 6/7/2014 | 3717.4976 | 42700.4453 | 2.014% | 3060 | 3121.2 | 3183.624 | 3247.2965 | 3312.2424 | 3378.4873 | 3446.057 | 3514.9781 | 3585.2777 | 3656.9833 | 3730.1229 | 3804.7254 | 3880.8199 | 3958.4363 | 4037.605 | 4118.3571 | 4200.7243 | 4284.7387 | 4370.4335 | 4457.8422 | 4546.999 | 4637.939 | 4730.6978 | 4825.3117 | 4921.818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42700.4453 | 2.014% | 3060 | 3121.2 | 3183.624 | 3247.2965 | 3312.2424 | 3378.4873 | 3446.057 | 3514.9781 | 3585.2777 | 3656.9833 | 3730.1229 | 3804.7254 | 3880.8199 | 3958.4363 | 4037.605 | 4118.3571 | 4200.7243 | 4284.7387 | 4370.4335 | 4457.8422 | 4546.999 | 4637.939 | 4730.6978 | 4825.3117 | 4921.818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manage inventory of spare parts | Administration | Management | Asset Management | 1 | 0 | 0 | Monitoring |  | Administrator | 22.9956 | 0.5 | 1 | interval | 1 | 1 | 2 | 0 | 22.9956 | 0 | 22.9956 |  |  | 56.9907 | 654.6143 | 0.03087% | 46.911 | 47.8492 | 48.8062 | 49.7823 | 50.778 | 51.7935 | 52.8294 | 53.886 | 54.9637 | 56.063 | 57.1842 | 58.3279 | 59.4945 | 60.6844 | 61.898 | 63.136 | 64.3987 | 65.6867 | 67.0004 | 68.3404 | 69.7072 | 71.1014 | 72.5234 | 73.9739 | 75.4534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 654.6143 | 0.03087% | 46.911 | 47.8492 | 48.8062 | 49.7823 | 50.778 | 51.7935 | 52.8294 | 53.886 | 54.9637 | 56.063 | 57.1842 | 58.3279 | 59.4945 | 60.6844 | 61.898 | 63.136 | 64.3987 | 65.6867 | 67.0004 | 68.3404 | 69.7072 | 71.1014 | 72.5234 | 73.9739 | 75.4534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meet with key site staff to continue awareness, question any issues, and report on findings. | Administration | Management | Documents | 1 | 0 | 0 | N/A |  | Administrator | 22.9956 | 1 | 1 | interval | 1 | 2 | 2 | 0 | 45.9912 | 0 | 45.9912 |  |  | 56.9907 | 654.6143 | 0.03087% | 46.911 | 47.8492 | 48.8062 | 49.7823 | 50.778 | 51.7935 | 52.8294 | 53.886 | 54.9637 | 56.063 | 57.1842 | 58.3279 | 59.4945 | 60.6844 | 61.898 | 63.136 | 64.3987 | 65.6867 | 67.0004 | 68.3404 | 69.7072 | 71.1014 | 72.5234 | 73.9739 | 75.4534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 654.6143 | 0.03087% | 46.911 | 47.8492 | 48.8062 | 49.7823 | 50.778 | 51.7935 | 52.8294 | 53.886 | 54.9637 | 56.063 | 57.1842 | 58.3279 | 59.4945 | 60.6844 | 61.898 | 63.136 | 64.3987 | 65.6867 | 67.0004 | 68.3404 | 69.7072 | 71.1014 | 72.5234 | 73.9739 | 75.4534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Confirm availability and take any measures to secure operating instructions, warranties and performance guarantees, and other project documentation. | Administration | Management | Documents | 1 | 0 | 0 | N/A |  | Administrator | 22.9956 | 1 | 1 | interval | 1 | 100.08 | 100.08 | 0 | 2301.3973 | 0 | 2301.3973 |  |  | 2851.813 | 32756.8971 | 1.545% | 2347.4253 | 2394.3738 | 2442.2613 | 2491.1065 | 2540.9286 | 2591.7472 | 2643.5821 | 2696.4538 | 2750.3829 | 2805.3905 | 2861.4983 | 2918.7283 | 2977.1029 | 3036.6449 | 3097.3778 | 3159.3254 | 3222.5119 | 3286.9621 | 3352.7014 | 3419.7554 | 3488.1505 | 3557.9135 | 3629.0718 | 3701.6532 | 3775.6863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32756.8971 | 1.545% | 2347.4253 | 2394.3738 | 2442.2613 | 2491.1065 | 2540.9286 | 2591.7472 | 2643.5821 | 2696.4538 | 2750.3829 | 2805.3905 | 2861.4983 | 2918.7283 | 2977.1029 | 3036.6449 | 3097.3778 | 3159.3254 | 3222.5119 | 3286.9621 | 3352.7014 | 3419.7554 | 3488.1505 | 3557.9135 | 3629.0718 | 3701.6532 | 3775.6863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Document all O&M activities in a workbook available to all service personnel. | Administration | Management | Documents | 1 | 0 | 0 | N/A |  | Administrator | 22.9956 | 0.08 | 1 | interval | 1 | 0.25 | 3.125 | 0 | 5.7489 | 0 | 5.7489 |  |  | 89.0479 | 1022.8348 | 0.04824% | 73.2984 | 74.7644 | 76.2597 | 77.7848 | 79.3405 | 80.9274 | 82.5459 | 84.1968 | 85.8808 | 87.5984 | 89.3503 | 91.1373 | 92.9601 | 94.8193 | 96.7157 | 98.65 | 100.623 | 102.6355 | 104.6882 | 106.7819 | 108.9176 | 111.0959 | 113.3178 | 115.5842 | 117.8959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1022.8348 | 0.04824% | 73.2984 | 74.7644 | 76.2597 | 77.7848 | 79.3405 | 80.9274 | 82.5459 | 84.1968 | 85.8808 | 87.5984 | 89.3503 | 91.1373 | 92.9601 | 94.8193 | 96.7157 | 98.65 | 100.623 | 102.6355 | 104.6882 | 106.7819 | 108.9176 | 111.0959 | 113.3178 | 115.5842 | 117.8959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Review O&M agreements and ensure that services are actually provided | Administration | Management | Documents | 1 | 0 | 0 | N/A |  | Administrator | 22.9956 | 1 | 1 | interval | 1 | 1 | 1 | 0 | 22.9956 | 0 | 22.9956 |  |  | 28.4953 | 327.3071 | 0.01544% | 23.4555 | 23.9246 | 24.4031 | 24.8912 | 25.389 | 25.8968 | 26.4147 | 26.943 | 27.4818 | 28.0315 | 28.5921 | 29.164 | 29.7472 | 30.3422 | 30.949 | 31.568 | 32.1994 | 32.8433 | 33.5002 | 34.1702 | 34.8536 | 35.5507 | 36.2617 | 36.9869 | 37.7267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327.3071 | 0.01544% | 23.4555 | 23.9246 | 24.4031 | 24.8912 | 25.389 | 25.8968 | 26.4147 | 26.943 | 27.4818 | 28.0315 | 28.5921 | 29.164 | 29.7472 | 30.3422 | 30.949 | 31.568 | 32.1994 | 32.8433 | 33.5002 | 34.1702 | 34.8536 | 35.5507 | 36.2617 | 36.9869 | 37.7267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Update record with preventative maintenance activities and track any problems or warranty issues and secure the record on-site. | Administration | Management | Documents | 1 | 0 | 0 | N/A |  | Administrator | 22.9956 | 0.08 | 1 | interval | 1 | 0.25 | 3.125 | 0 | 5.7489 | 0 | 5.7489 |  |  | 89.0479 | 1022.8348 | 0.04824% | 73.2984 | 74.7644 | 76.2597 | 77.7848 | 79.3405 | 80.9274 | 82.5459 | 84.1968 | 85.8808 | 87.5984 | 89.3503 | 91.1373 | 92.9601 | 94.8193 | 96.7157 | 98.65 | 100.623 | 102.6355 | 104.6882 | 106.7819 | 108.9176 | 111.0959 | 113.3178 | 115.5842 | 117.8959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1022.8348 | 0.04824% | 73.2984 | 74.7644 | 76.2597 | 77.7848 | 79.3405 | 80.9274 | 82.5459 | 84.1968 | 85.8808 | 87.5984 | 89.3503 | 91.1373 | 92.9601 | 94.8193 | 96.7157 | 98.65 | 100.623 | 102.6355 | 104.6882 | 106.7819 | 108.9176 | 111.0959 | 113.3178 | 115.5842 | 117.8959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maintain a log of cumulative power delivery (kWh to date) and chart this value against date. Chart the value even for uneven or infrequent intervals. Explain variation by season or weather. | Administration | Management | Meter | 1 | 0 | 0 | N/A |  | Administrator | 22.9956 | 0.08 | 1 | interval | 1 | 0.05 | 0.625 | 0 | 1.1498 | 0 | 1.1498 |  |  | 17.8096 | 204.567 | 0.009648% | 14.6597 | 14.9529 | 15.2519 | 15.557 | 15.8681 | 16.1855 | 16.5092 | 16.8394 | 17.1762 | 17.5197 | 17.8701 | 18.2275 | 18.592 | 18.9639 | 19.3431 | 19.73 | 20.1246 | 20.5271 | 20.9376 | 21.3564 | 21.7835 | 22.2192 | 22.6636 | 23.1168 | 23.5792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204.567 | 0.009648% | 14.6597 | 14.9529 | 15.2519 | 15.557 | 15.8681 | 16.1855 | 16.5092 | 16.8394 | 17.1762 | 17.5197 | 17.8701 | 18.2275 | 18.592 | 18.9639 | 19.3431 | 19.73 | 20.1246 | 20.5271 | 20.9376 | 21.3564 | 21.7835 | 22.2192 | 22.6636 | 23.1168 | 23.5792 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace protective devices (breakers) in building panel | Corrective | Repair | AC wiring | 1 | 1 | 1 | N/A |  | Master electrician | 32.012 | 25 | 3 | Weibull | 3 | 0.25 | 0.03 | 10 | 24.009 | 30 | 54.009 |  |  | 1.5378 | 15.6769 | 0.0007394% | 0.010576 | 0.043133 | 0.098869 | 0.17886 | 0.28394 | 0.41464 | 0.57099 | 0.75252 | 0.95806 | 1.1857 | 1.4327 | 1.6955 | 1.9697 | 2.2499 | 2.5301 | 2.8039 | 3.0642 | 3.3038 | 3.5159 | 3.6938 | 3.8318 | 3.9252 | 3.9705 | 3.966 | 3.9116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.1425 | 0.002082% | 0.010576 | 0.043133 | 0.098869 | 0.17886 | 0.28394 | 0.41464 | 0.57099 | 0.75252 | 0.95806 | 1.1857 | 1.4654 | 2.5643 | 3.9445 | 5.5217 | 7.2 | 8.8865 | 10.4988 | 11.9672 | 13.2342 | 14.2529 | 14.9855 | 15.4017 | 15.4789 | 15.2024 | 14.5677 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter AC fuse(s) | Corrective | Repair | AC wiring | 1 | 1 | 1 | EPC |  | Journeyman electrician | 19.9038 | 25 | 1 | Weibull | 30 | 0.15 | 0.18 | 10 | 89.5673 | 300 | 389.5673 |  |  | 11.927 | 136.547 | 0.00644% | 0 | 14.9658 | 14.6665 | 14.3733 | 14.0859 | 13.8043 | 13.5282 | 13.2577 | 12.9927 | 12.7329 | 12.4783 | 12.2288 | 11.9843 | 11.7446 | 11.5098 | 11.2797 | 11.0541 | 10.8331 | 10.6165 | 10.4042 | 10.1962 | 9.9923 | 9.7925 | 9.5967 | 9.4049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 276.8968 | 0.01306% | 0 | 46.0565 | 42.8418 | 39.7019 | 36.6483 | 33.6921 | 30.8433 | 28.111 | 25.5033 | 23.0272 | 20.6883 | 18.4909 | 16.438 | 14.5313 | 12.771 | 11.2797 | 11.0541 | 10.8331 | 10.6165 | 10.4042 | 10.1962 | 9.9923 | 9.7925 | 9.5967 | 9.4049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Locate line-to-line fault | Corrective | Repair | AC Wiring | 1 | 1 | 1 | EPC |  | Master electrician | 32.012 | 25 | 3 | Weibull | 1 | 1 | 0.04 | 0 | 32.012 | 0 | 32.012 |  |  | 0.91119 | 9.2861 | 0.000438% | 0 | 0.025565 | 0.058601 | 0.10601 | 0.1683 | 0.24576 | 0.33844 | 0.44603 | 0.56786 | 0.70278 | 0.84919 | 1.005 | 1.1674 | 1.3335 | 1.4997 | 1.6619 | 1.8162 | 1.9582 | 2.0839 | 2.1894 | 2.2712 | 2.3265 | 2.3534 | 2.3507 | 2.3185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.1581 | 0.001234% | 0 | 0.025565 | 0.058601 | 0.10601 | 0.1683 | 0.24576 | 0.33844 | 0.44603 | 0.56786 | 0.70278 | 0.86858 | 1.5199 | 2.3379 | 3.2728 | 4.2676 | 5.2672 | 6.2228 | 7.0932 | 7.8441 | 8.4479 | 8.8821 | 9.1288 | 9.1746 | 9.0107 | 8.6345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Locate underground AC wiring | Corrective | Repair | AC Wiring | 1 | 0 | 0 | N/A |  | Utilities locator | 25.5499 | 25 | 3 | Weibull | 1 | 4 | 0.16 | 0 | 102.1996 | 0 | 102.1996 |  |  | 2.91 | 29.6649 | 0.001399% | 0.020013 | 0.081618 | 0.18709 | 0.33845 | 0.5373 | 0.7846 | 1.0805 | 1.424 | 1.8129 | 2.2437 | 2.7111 | 3.2084 | 3.7271 | 4.2574 | 4.7877 | 5.3057 | 5.7982 | 6.2517 | 6.653 | 6.9896 | 7.2508 | 7.4275 | 7.5133 | 7.5048 | 7.4019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5296 | 0.00394% | 0.020013 | 0.081618 | 0.18709 | 0.33845 | 0.5373 | 0.7846 | 1.0805 | 1.424 | 1.8129 | 2.2437 | 2.773 | 4.8523 | 7.464 | 10.4486 | 13.6244 | 16.8157 | 19.8666 | 22.6452 | 25.0427 | 26.9704 | 28.3566 | 29.1442 | 29.2902 | 28.767 | 27.5661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair line-to-line fault | Corrective | Repair | AC Wiring | 1 | 0 | 0 | N/A |  | Master electrician | 32.012 | 25 | 3 | Weibull | 1 | 1 | 0.04 | 20 | 32.012 | 20 | 52.012 |  |  | 1.481 | 15.0972 | 0.0007121% | 0.010185 | 0.041538 | 0.095213 | 0.17225 | 0.27345 | 0.39931 | 0.54988 | 0.7247 | 0.92263 | 1.1419 | 1.3797 | 1.6328 | 1.8968 | 2.1667 | 2.4366 | 2.7002 | 2.9509 | 3.1817 | 3.3859 | 3.5572 | 3.6901 | 3.78 | 3.8237 | 3.8194 | 3.767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.5104 | 0.002005% | 0.010185 | 0.041538 | 0.095213 | 0.17225 | 0.27345 | 0.39931 | 0.54988 | 0.7247 | 0.92263 | 1.1419 | 1.4112 | 2.4694 | 3.7986 | 5.3175 | 6.9338 | 8.5579 | 10.1106 | 11.5247 | 12.7449 | 13.7259 | 14.4314 | 14.8322 | 14.9065 | 14.6403 | 14.0291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace broken/crushed AC wiring conduit and fittings | Corrective | Repair | AC wiring | 1 | 0 | 0 | N/A | strings | Journeyman electrician | 19.9038 | 25 | 3 | Weibull | 2341.9204 | 0.25 | 23.4192 | 10 | 11653.3057 | 23419.2037 | 35072.5095 |  |  | 998.6442 | 10180.2859 | 0.4802% | 6.8682 | 28.0095 | 64.2038 | 116.1475 | 184.3888 | 269.2576 | 370.7932 | 488.6731 | 622.1458 | 769.972 | 930.38 | 1101.0401 | 1279.0624 | 1461.0245 | 1643.0302 | 1820.8035 | 1989.8152 | 2145.4412 | 2283.146 | 2398.6823 | 2488.2968 | 2548.9287 | 2578.3851 | 2575.4831 | 2540.1414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28665.3947 | 1.352% | 6.8682 | 28.0095 | 64.2038 | 116.1475 | 184.3888 | 269.2576 | 370.7932 | 488.6731 | 622.1458 | 769.972 | 951.6211 | 1665.1824 | 2561.4607 | 3585.6979 | 4675.5645 | 5770.7545 | 6817.7507 | 7771.2923 | 8594.0525 | 9255.6 | 9731.3089 | 10001.5952 | 10051.7006 | 9872.1586 | 9460.0308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace MC connector lead to combiner box | Corrective | Repair | DC wiring | 1 | 1 | 1 | EPC | modules | PV module/array Specialist | 33.1731 | 25 | 1 | Weibull | 32787 | 0.1 | 131.148 | 20 | 108764.5673 | 655740 | 764504.5673 |  |  | 23406.1609 | 267966.0691 | 12.64% | 0 | 29369.5208 | 28782.2839 | 28206.7887 | 27642.8004 | 27090.0889 | 26548.4288 | 26017.599 | 25497.383 | 24987.5687 | 24487.9479 | 23998.317 | 23518.4761 | 23048.2295 | 22587.3854 | 22135.7558 | 21693.1564 | 21259.4067 | 20834.3297 | 20417.752 | 20009.5037 | 19609.4183 | 19217.3324 | 18833.0862 | 18456.523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 543394.881 | 25.63% | 0 | 90383.2893 | 84074.638 | 77912.7417 | 71920.3723 | 66118.9495 | 60528.2795 | 55166.3083 | 50048.8954 | 45189.6145 | 40599.5855 | 36287.3444 | 32258.7547 | 28516.9642 | 25062.4093 | 22135.7558 | 21693.1564 | 21259.4067 | 20834.3297 | 20417.752 | 20009.5037 | 19609.4183 | 19217.3324 | 18833.0862 | 18456.523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace MC Connectors between modules | Corrective | Repair | DC wiring | 1 | 1 | 1 | Module (Product) | modules | PV module/array Specialist | 33.1731 | 25 | 3 | Weibull | 32787 | 0.1 | 131.148 | 5 | 108764.5673 | 163935 | 272699.5673 |  |  | 0 | 20961.8581 | 0.9887% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19347.2747 | 19818.7057 | 20047.739 | 20025.175 | 19750.3823 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80998.2665 | 3.82% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75663.9247 | 77765.4839 | 78155.0691 | 76759.0751 | 73554.6542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Locate ground fault | Corrective | Repair | DC Wiring | 1 | 1 | 1 | EPC |  | Master electrician | 32.012 | 25 | 3 | Weibull | 1 | 4 | 0.16 | 0 | 128.0481 | 0 | 128.0481 |  |  | 3.6447 | 37.1443 | 0.001752% | 0 | 0.10226 | 0.2344 | 0.42405 | 0.67319 | 0.98305 | 1.3537 | 1.7841 | 2.2714 | 2.8111 | 3.3968 | 4.0198 | 4.6698 | 5.3341 | 5.9986 | 6.6477 | 7.2647 | 7.8329 | 8.3357 | 8.7575 | 9.0847 | 9.306 | 9.4136 | 9.403 | 9.2739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.6326 | 0.004935% | 0 | 0.10226 | 0.2344 | 0.42405 | 0.67319 | 0.98305 | 1.3537 | 1.7841 | 2.2714 | 2.8111 | 3.4743 | 6.0795 | 9.3518 | 13.0912 | 17.0703 | 21.0688 | 24.8913 | 28.3726 | 31.3765 | 33.7918 | 35.5285 | 36.5154 | 36.6983 | 36.0428 | 34.5381 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair ground fault | Corrective | Repair | DC Wiring | 1 | 1 | 1 | EPC |  | Master electrician | 32.012 | 25 | 3 | Weibull | 1 | 1 | 0.04 | 20 | 32.012 | 20 | 52.012 |  |  | 1.4805 | 15.0877 | 0.0007116% | 0 | 0.041538 | 0.095213 | 0.17225 | 0.27345 | 0.39931 | 0.54988 | 0.7247 | 0.92263 | 1.1419 | 1.3797 | 1.6328 | 1.8968 | 2.1667 | 2.4366 | 2.7002 | 2.9509 | 3.1817 | 3.3859 | 3.5572 | 3.6901 | 3.78 | 3.8237 | 3.8194 | 3.767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.5008 | 0.002005% | 0 | 0.041538 | 0.095213 | 0.17225 | 0.27345 | 0.39931 | 0.54988 | 0.7247 | 0.92263 | 1.1419 | 1.4112 | 2.4694 | 3.7986 | 5.3175 | 6.9338 | 8.5579 | 10.1106 | 11.5247 | 12.7449 | 13.7259 | 14.4314 | 14.8322 | 14.9065 | 14.6403 | 14.0291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace fuse(s) on DC source circuits to inverter | Corrective | Repair | DC wiring | 1 | 1 | 1 | EPC |  | Master electrician | 32.012 | 25 | 3 | Weibull | 157 | 0.08 | 0.5024 | 5 | 402.071 | 785 | 1187.071 |  |  | 33.7887 | 344.3467 | 0.01624% | 0 | 0.94802 | 2.1731 | 3.9312 | 6.2409 | 9.1133 | 12.5499 | 16.5397 | 21.0573 | 26.0606 | 31.4898 | 37.266 | 43.2914 | 49.4501 | 55.6103 | 61.6273 | 67.3477 | 72.615 | 77.2758 | 81.1863 | 84.2194 | 86.2715 | 87.2685 | 87.1703 | 85.9741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 969.9973 | 0.04575% | 0 | 0.94802 | 2.1731 | 3.9312 | 6.2409 | 9.1133 | 12.5499 | 16.5397 | 21.0573 | 26.0606 | 32.2088 | 56.3601 | 86.6957 | 121.3622 | 158.2501 | 195.3181 | 230.7549 | 263.0287 | 290.876 | 313.2668 | 329.3678 | 338.5159 | 340.2118 | 334.135 | 320.186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seal Leaking Junction Box | Corrective | Repair | DC Wiring | 1 | 1 | 0 | Module (Product) | modules | Journeyman electrician | 19.9038 | 25 | 3 | Weibull | 32787 | 0.25 | 327.87 | 10 | 163146.851 | 327870 | 491016.851 |  |  | 4645.3951 | 72558.3494 | 3.422% | 31.9486 | 130.292 | 298.6569 | 540.2835 | 857.7218 | 1252.5059 | 1724.8192 | 2273.1616 | 2894.0368 | 3581.6801 | 4327.8504 | 5121.71 | 5949.8167 | 6796.2499 | 7642.8865 | 8469.8349 | 9256.0268 | 9979.9526 | 10620.514 | 11157.9542 | 34836.2778 | 35685.1262 | 36097.5184 | 36056.8903 | 35562.1046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230728.0635 | 10.88% | 31.9486 | 130.292 | 298.6569 | 540.2835 | 857.7218 | 1252.5059 | 1724.8192 | 2273.1616 | 2894.0368 | 3581.6801 | 4426.6573 | 7745.9319 | 11915.151 | 16679.5969 | 21749.3312 | 26843.8284 | 31714.1422 | 36149.7334 | 39976.9682 | 43054.2899 | 136238.8008 | 140022.8222 | 140724.3008 | 138210.7046 | 132440.8947 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Locate underground DC wiring | Corrective | Repair | DC wiring | 1 | 1 | 1 | N/A |  | Utilities locator | 25.5499 | 25 | 3 | Weibull | 1 | 2 | 0.08 | 0 | 51.0998 | 0 | 51.0998 |  |  | 1.455 | 14.8324 | 0.0006996% | 0.010007 | 0.040809 | 0.093543 | 0.16922 | 0.26865 | 0.3923 | 0.54024 | 0.71199 | 0.90645 | 1.1218 | 1.3555 | 1.6042 | 1.8636 | 2.1287 | 2.3939 | 2.6529 | 2.8991 | 3.1259 | 3.3265 | 3.4948 | 3.6254 | 3.7137 | 3.7566 | 3.7524 | 3.7009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.7648 | 0.00197% | 0.010007 | 0.040809 | 0.093543 | 0.16922 | 0.26865 | 0.3923 | 0.54024 | 0.71199 | 0.90645 | 1.1218 | 1.3865 | 2.4261 | 3.732 | 5.2243 | 6.8122 | 8.4079 | 9.9333 | 11.3226 | 12.5213 | 13.4852 | 14.1783 | 14.5721 | 14.6451 | 14.3835 | 13.783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace broken/crushed DC wiring conduit and fittings | Corrective | Repair | DC wiring | 1 | 1 | 1 | N/A |  | Journeyman electrician | 19.9038 | 25 | 3 | Weibull | 1 | 4 | 0.16 | 100 | 79.6154 | 100 | 179.6154 |  |  | 5.1143 | 52.1359 | 0.002459% | 0.035174 | 0.14344 | 0.3288 | 0.59482 | 0.9443 | 1.3789 | 1.8989 | 2.5026 | 3.1862 | 3.9432 | 4.7647 | 5.6387 | 6.5504 | 7.4823 | 8.4144 | 9.3248 | 10.1904 | 10.9874 | 11.6926 | 12.2843 | 12.7432 | 13.0537 | 13.2046 | 13.1897 | 13.0087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146.8029 | 0.006924% | 0.035174 | 0.14344 | 0.3288 | 0.59482 | 0.9443 | 1.3789 | 1.8989 | 2.5026 | 3.1862 | 3.9432 | 4.8735 | 8.5278 | 13.1179 | 18.3633 | 23.9448 | 29.5535 | 34.9155 | 39.7988 | 44.0124 | 47.4003 | 49.8365 | 51.2208 | 51.4774 | 50.5579 | 48.4473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace failed DC fuses in combiner box | Corrective | Repair | DC wiring | 1 | 1 | 1 | N/A | strings | Journeyman electrician | 19.9038 | 25 | 3 | Weibull | 2341.9204 | 0.08 | 7.4941 | 1 | 3729.0578 | 2341.9204 | 6070.9782 |  |  | 172.8632 | 1762.1862 | 0.08311% | 1.1889 | 4.8484 | 11.1135 | 20.1049 | 31.9173 | 46.6079 | 64.1835 | 84.5883 | 107.6921 | 133.2805 | 161.0468 | 190.5877 | 221.403 | 252.9003 | 284.4051 | 315.1773 | 344.4329 | 371.3714 | 395.2078 | 415.2069 | 430.719 | 441.2142 | 446.3131 | 445.8108 | 439.6932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4961.92 | 0.234% | 1.1889 | 4.8484 | 11.1135 | 20.1049 | 31.9173 | 46.6079 | 64.1835 | 84.5883 | 107.6921 | 133.2805 | 164.7236 | 288.2396 | 443.3835 | 620.6768 | 809.3305 | 998.9056 | 1180.1384 | 1345.1945 | 1487.6125 | 1602.125 | 1684.4693 | 1731.2553 | 1739.9284 | 1708.8501 | 1637.5116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-route conduit | Corrective | Repair | DC wiring | 1 | 1 | 1 | N/A |  | Journeyman electrician | 19.9038 | 25 | 3 | Weibull | 1 | 4 | 0.16 | 100 | 79.6154 | 100 | 179.6154 |  |  | 5.1143 | 52.1359 | 0.002459% | 0.035174 | 0.14344 | 0.3288 | 0.59482 | 0.9443 | 1.3789 | 1.8989 | 2.5026 | 3.1862 | 3.9432 | 4.7647 | 5.6387 | 6.5504 | 7.4823 | 8.4144 | 9.3248 | 10.1904 | 10.9874 | 11.6926 | 12.2843 | 12.7432 | 13.0537 | 13.2046 | 13.1897 | 13.0087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146.8029 | 0.006924% | 0.035174 | 0.14344 | 0.3288 | 0.59482 | 0.9443 | 1.3789 | 1.8989 | 2.5026 | 3.1862 | 3.9432 | 4.8735 | 8.5278 | 13.1179 | 18.3633 | 23.9448 | 29.5535 | 34.9155 | 39.7988 | 44.0124 | 47.4003 | 49.8365 | 51.2208 | 51.4774 | 50.5579 | 48.4473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter | Corrective | Repair | Inverter | 0 | 1 | 1 | Inverter | Inverter | Inverter specialist | 33.1731 | 25 | 2 | Weibull | 10 | 250.5 | 100.2 | 190000 | 83098.5577 | 1900000 | 0 | formula for inverter labor |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Start/stop inverter (reboot to clear unknown error) | Corrective | Repair | Inverter | 1 | 0 | 0 | EPC | inverter | Inspector | 33.12 | 1 | 3 | Interval | 10 | 0.25 | 2.5 | 0 | 82.8 | 0 | 82.8 |  |  | 102.6029 | 1178.5323 | 0.05559% | 84.456 | 86.1451 | 87.868 | 89.6254 | 91.4179 | 93.2462 | 95.1112 | 97.0134 | 98.9537 | 100.9327 | 102.9514 | 105.0104 | 107.1106 | 109.2528 | 111.4379 | 113.6667 | 115.94 | 118.2588 | 120.624 | 123.0364 | 125.4972 | 128.0071 | 130.5673 | 133.1786 | 135.8422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1178.5323 | 0.05559% | 84.456 | 86.1451 | 87.868 | 89.6254 | 91.4179 | 93.2462 | 95.1112 | 97.0134 | 98.9537 | 100.9327 | 102.9514 | 105.0104 | 107.1106 | 109.2528 | 111.4379 | 113.6667 | 115.94 | 118.2588 | 120.624 | 123.0364 | 125.4972 | 128.0071 | 130.5673 | 133.1786 | 135.8422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter fan motor | Corrective | Repair | Inverter | 1 | 1 | 0 | Inverter | inverter | Inverter specialist | 33.1731 | 15 | 1 | Weibull | 10 | 1 | 0.66667 | 120 | 331.7308 | 1200 | 1531.7308 |  |  | 33.5413 | 343.9762 | 0.01622% | 21.1029 | 20.1367 | 19.2148 | 18.3351 | 17.4957 | 16.6947 | 15.9303 | 15.201 | 14.5051 | 13.841 | 60.9832 | 58.1912 | 55.5271 | 52.9849 | 50.5591 | 48.2444 | 46.0356 | 43.9279 | 41.9168 | 39.9977 | 38.1665 | 36.4191 | 34.7518 | 33.1607 | 31.6425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840.4676 | 0.03964% | 96.5982 | 89.8548 | 83.0527 | 76.2459 | 69.4907 | 62.8443 | 56.3641 | 50.1058 | 44.1221 | 38.4613 | 153.1389 | 130.5334 | 109.8963 | 91.306 | 74.7952 | 60.3509 | 47.9155 | 43.9279 | 41.9168 | 39.9977 | 38.1665 | 36.4191 | 34.7518 | 33.1607 | 31.6425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
manual reset of arc-fault trip (NEC 690.11) | Corrective | Repair | Inverter | 1 | 1 | 1 | EPC | inverter | Inverter specialist | 33.1731 | 25 | 1 | Weibull | 10 | 0.08 | 0.032 | 0 | 26.5385 | 0 | 26.5385 |  |  | 0.8125 | 9.302 | 0.0004387% | 0 | 1.0195 | 0.99913 | 0.97915 | 0.95957 | 0.94039 | 0.92158 | 0.90316 | 0.8851 | 0.8674 | 0.85006 | 0.83306 | 0.8164 | 0.80008 | 0.78408 | 0.7684 | 0.75304 | 0.73798 | 0.72323 | 0.70877 | 0.6946 | 0.68071 | 0.6671 | 0.65376 | 0.64069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.863 | 0.0008897% | 0 | 3.1375 | 2.9185 | 2.7046 | 2.4966 | 2.2952 | 2.1011 | 1.915 | 1.7374 | 1.5687 | 1.4093 | 1.2597 | 1.1198 | 0.98992 | 0.87 | 0.7684 | 0.75304 | 0.73798 | 0.72323 | 0.70877 | 0.6946 | 0.68071 | 0.6671 | 0.65376 | 0.64069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RE-install inverter control software | Corrective | Repair | Inverter | 1 | 1 | 1 | EPC | inverter | Inverter specialist | 33.1731 | 20 | 1 | Weibull | 10 | 1 | 0.5 | 0 | 331.7308 | 0 | 331.7308 |  |  | 11.4589 | 132.3281 | 0.006241% | 0 | 15.6144 | 15.15 | 14.6993 | 14.2621 | 13.8378 | 13.4262 | 13.0268 | 12.6394 | 12.2634 | 11.8986 | 11.5447 | 11.2013 | 10.8681 | 10.5448 | 10.2311 | 9.9268 | 9.6315 | 9.345 | 9.067 | 8.7973 | 8.5356 | 8.2817 | 8.0354 | 7.7964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338.6144 | 0.01597% | 0 | 59.3999 | 55.1249 | 50.9103 | 46.7791 | 42.7536 | 38.8552 | 35.1039 | 31.5181 | 28.1141 | 24.9059 | 21.905 | 19.1198 | 16.5559 | 14.216 | 12.0995 | 10.203 | 9.6315 | 9.345 | 9.067 | 8.7973 | 8.5356 | 8.2817 | 8.0354 | 7.7964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace 24VDC power supply for inverter controls | Corrective | Repair | Inverter | 1 | 1 | 1 | EPC | inverter | Inverter specialist | 33.1731 | 20 | 1 | Weibull | 10 | 1 | 0.5 | 120 | 331.7308 | 1200 | 1531.7308 |  |  | 52.9103 | 611.0107 | 0.02882% | 0 | 72.098 | 69.9534 | 67.8726 | 65.8536 | 63.8947 | 61.9941 | 60.1501 | 58.3608 | 56.6248 | 54.9405 | 53.3062 | 51.7206 | 50.1821 | 48.6894 | 47.2411 | 45.8358 | 44.4724 | 43.1495 | 41.866 | 40.6206 | 39.4123 | 38.24 | 37.1025 | 35.9989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1563.5151 | 0.07374% | 0 | 274.2724 | 254.5331 | 235.0728 | 215.9974 | 197.41 | 179.4095 | 162.0883 | 145.5313 | 129.8138 | 115.0004 | 101.1438 | 88.2834 | 76.4451 | 65.6408 | 55.8681 | 47.1111 | 44.4724 | 43.1495 | 41.866 | 40.6206 | 39.4123 | 38.24 | 37.1025 | 35.9989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace AC contactor in inverter | Corrective | Repair | Inverter | 1 | 1 | 0 | Inverter | inverter | Inverter specialist | 33.1731 | 20 | 1 | Weibull | 10 | 2 | 1 | 40 | 663.4615 | 400 | 1063.4615 |  |  | 30.8129 | 351.0085 | 0.01656% | 32.1863 | 31.2289 | 30.3 | 29.3987 | 28.5242 | 27.6757 | 26.8524 | 26.0537 | 25.2787 | 24.5268 | 38.1445 | 37.0098 | 35.9089 | 34.8408 | 33.8044 | 32.7989 | 31.8232 | 30.8766 | 29.9582 | 29.067 | 28.2024 | 27.3635 | 26.5495 | 25.7598 | 24.9936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 874.6815 | 0.04125% | 127.4242 | 118.7997 | 110.2497 | 101.8206 | 93.5582 | 85.5072 | 77.7103 | 70.2077 | 63.0361 | 56.2282 | 79.8433 | 70.2228 | 61.294 | 53.0749 | 45.5736 | 38.7885 | 32.7087 | 30.8766 | 29.9582 | 29.067 | 28.2024 | 27.3635 | 26.5495 | 25.7598 | 24.9936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace capacitors in inverter | Corrective | Repair | Inverter | 1 | 1 | 0 | Inverter | inverter | Inverter specialist | 33.1731 | 20 | 1 | Weibull | 10 | 2 | 1 | 30000 | 663.4615 | 300000 | 300663.4615 |  |  | 4738.8362 | 42498.4135 | 2.004% | 32.1863 | 31.2289 | 30.3 | 29.3987 | 28.5242 | 27.6757 | 26.8524 | 26.0537 | 25.2787 | 24.5268 | 10784.2658 | 10463.4771 | 10152.2307 | 9850.2426 | 9557.2374 | 9272.9479 | 8997.1149 | 8729.4869 | 8469.8197 | 8217.8765 | 7973.4277 | 7736.2502 | 7506.1278 | 7282.8506 | 7066.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59569.875 | 2.81% | 127.4242 | 118.7997 | 110.2497 | 101.8206 | 93.5582 | 85.5072 | 77.7103 | 70.2077 | 63.0361 | 56.2282 | 22573.4305 | 19853.5089 | 17329.1457 | 15005.4152 | 12884.6314 | 10966.3506 | 9247.4466 | 8729.4869 | 8469.8197 | 8217.8765 | 7973.4277 | 7736.2502 | 7506.1278 | 7282.8506 | 7066.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace DC contactor in inverter | Corrective | Repair | Inverter | 1 | 1 | 0 | Inverter | inverter | Inverter specialist | 33.1731 | 20 | 1 | Weibull | 10 | 2 | 1 | 40 | 663.4615 | 400 | 1063.4615 |  |  | 30.8129 | 351.0085 | 0.01656% | 32.1863 | 31.2289 | 30.3 | 29.3987 | 28.5242 | 27.6757 | 26.8524 | 26.0537 | 25.2787 | 24.5268 | 38.1445 | 37.0098 | 35.9089 | 34.8408 | 33.8044 | 32.7989 | 31.8232 | 30.8766 | 29.9582 | 29.067 | 28.2024 | 27.3635 | 26.5495 | 25.7598 | 24.9936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 874.6815 | 0.04125% | 127.4242 | 118.7997 | 110.2497 | 101.8206 | 93.5582 | 85.5072 | 77.7103 | 70.2077 | 63.0361 | 56.2282 | 79.8433 | 70.2228 | 61.294 | 53.0749 | 45.5736 | 38.7885 | 32.7087 | 30.8766 | 29.9582 | 29.067 | 28.2024 | 27.3635 | 26.5495 | 25.7598 | 24.9936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace fuses internal to inverter | Corrective | Repair | Inverter | 1 | 0 | 0 | Inverter | inverter | Inverter specialist | 33.1731 | 20 | 1 | Weibull | 10 | 0.25 | 0.125 | 25 | 82.9327 | 250 | 332.9327 |  |  | 12.308 | 147.9024 | 0.006976% | 16.1515 | 15.671 | 15.2049 | 14.7526 | 14.3138 | 13.888 | 13.4749 | 13.074 | 12.6851 | 12.3078 | 11.9417 | 11.5865 | 11.2418 | 10.9074 | 10.583 | 10.2682 | 9.9627 | 9.6664 | 9.3789 | 9.0999 | 8.8292 | 8.5666 | 8.3117 | 8.0645 | 7.8246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 399.601 | 0.01885% | 63.9429 | 59.6151 | 55.3246 | 51.0948 | 46.9486 | 42.9085 | 38.9959 | 35.2311 | 31.6323 | 28.216 | 24.9962 | 21.9843 | 19.189 | 16.6159 | 14.2675 | 12.1433 | 10.2399 | 9.6664 | 9.3789 | 9.0999 | 8.8292 | 8.5666 | 8.3117 | 8.0645 | 7.8246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace GFI components in inveter | Corrective | Repair | Inverter | 1 | 1 | 0 | Inverter | inverter | Inverter specialist | 33.1731 | 20 | 1 | Weibull | 10 | 1 | 0.5 | 120 | 331.7308 | 1200 | 1531.7308 |  |  | 31.1208 | 316.1832 | 0.01491% | 16.0932 | 15.6144 | 15.15 | 14.6993 | 14.2621 | 13.8378 | 13.4262 | 13.0268 | 12.6394 | 12.2634 | 54.9405 | 53.3062 | 51.7206 | 50.1821 | 48.6894 | 47.2411 | 45.8358 | 44.4724 | 43.1495 | 41.866 | 40.6206 | 39.4123 | 38.24 | 37.1025 | 35.9989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 633.2526 | 0.02987% | 63.7121 | 59.3999 | 55.1249 | 50.9103 | 46.7791 | 42.7536 | 38.8552 | 35.1039 | 31.5181 | 28.1141 | 115.0004 | 101.1438 | 88.2834 | 76.4451 | 65.6408 | 55.8681 | 47.1111 | 44.4724 | 43.1495 | 41.866 | 40.6206 | 39.4123 | 38.24 | 37.1025 | 35.9989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace IGBT driver card/board; diagnose with fault code | Corrective | Repair | Inverter | 1 | 1 | 0 | Inverter | inverter | Inverter specialist | 33.1731 | 20 | 1 | Weibull | 10 | 1 | 0.5 | 1000 | 331.7308 | 10000 | 10331.7308 |  |  | 169.4072 | 1554.1577 | 0.0733% | 16.0932 | 15.6144 | 15.15 | 14.6993 | 14.2621 | 13.8378 | 13.4262 | 13.0268 | 12.6394 | 12.2634 | 370.5809 | 359.5576 | 348.8622 | 338.4849 | 328.4164 | 318.6473 | 309.1688 | 299.9723 | 291.0493 | 282.3918 | 273.9917 | 265.8416 | 257.9339 | 250.2614 | 242.8171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2357.277 | 0.1112% | 63.7121 | 59.3999 | 55.1249 | 50.9103 | 46.7791 | 42.7536 | 38.8552 | 35.1039 | 31.5181 | 28.1141 | 775.6932 | 682.2283 | 595.4833 | 515.6327 | 442.756 | 376.8379 | 317.771 | 299.9723 | 291.0493 | 282.3918 | 273.9917 | 265.8416 | 257.9339 | 250.2614 | 242.8171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace IGBT matrix in inverter | Corrective | Repair | Inverter | 1 | 1 | 0 | Inverter | inverter | Inverter specialist | 33.1731 | 20 | 1 | Weibull | 10 | 4 | 2 | 100000 | 1326.9231 | 1000000 | 1001326.9231 |  |  | 15763.4179 | 141268.3959 | 6.663% | 64.3726 | 62.4578 | 60.5999 | 58.7973 | 57.0483 | 55.3514 | 53.7049 | 52.1074 | 50.5574 | 49.0535 | 35915.823 | 34847.4714 | 33810.8989 | 32805.1604 | 31829.3385 | 30882.5434 | 29963.9117 | 29072.6055 | 28207.8122 | 27368.743 | 26554.6327 | 25764.7389 | 24998.3414 | 24254.741 | 23533.2598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197504.4942 | 9.315% | 254.8484 | 237.5995 | 220.4995 | 203.6412 | 187.1164 | 171.0143 | 155.4207 | 140.4155 | 126.0723 | 112.4564 | 75178.3526 | 66119.9498 | 57712.8331 | 49973.9015 | 42910.8621 | 36522.2367 | 30797.614 | 29072.6055 | 28207.8122 | 27368.743 | 26554.6327 | 25764.7389 | 24998.3414 | 24254.741 | 23533.2598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inductors (coils) in inverter | Corrective | Repair | Inverter | 1 | 1 | 0 | Inverter | inverter | Inverter specialist | 33.1731 | 20 | 1 | Weibull | 10 | 4 | 2 | 50000 | 1326.9231 | 500000 | 501326.9231 |  |  | 7906.2361 | 70928.9348 | 3.345% | 64.3726 | 62.4578 | 60.5999 | 58.7973 | 57.0483 | 55.3514 | 53.7049 | 52.1074 | 50.5574 | 49.0535 | 17981.7087 | 17446.825 | 16927.852 | 16424.3163 | 15935.7588 | 15461.7339 | 15001.8094 | 14555.5658 | 14122.5961 | 13702.5055 | 13294.911 | 12899.4407 | 12515.7341 | 12143.4413 | 11782.2226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99548.5639 | 4.695% | 254.8484 | 237.5995 | 220.4995 | 203.6412 | 187.1164 | 171.0143 | 155.4207 | 140.4155 | 126.0723 | 112.4564 | 37638.9881 | 33103.7848 | 28894.6561 | 25020.0626 | 21483.8631 | 18285.3174 | 15419.2129 | 14555.5658 | 14122.5961 | 13702.5055 | 13294.911 | 12899.4407 | 12515.7341 | 12143.4413 | 11782.2226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter control card (PWM signal, voltage, phase, frequency, shut-down); diagnose with fault code | Corrective | Repair | Inverter | 1 | 1 | 0 | Inverter | inverter | Inverter specialist | 33.1731 | 20 | 1 | Weibull | 10 | 1 | 0.5 | 1000 | 331.7308 | 10000 | 10331.7308 |  |  | 169.4072 | 1554.1577 | 0.0733% | 16.0932 | 15.6144 | 15.15 | 14.6993 | 14.2621 | 13.8378 | 13.4262 | 13.0268 | 12.6394 | 12.2634 | 370.5809 | 359.5576 | 348.8622 | 338.4849 | 328.4164 | 318.6473 | 309.1688 | 299.9723 | 291.0493 | 282.3918 | 273.9917 | 265.8416 | 257.9339 | 250.2614 | 242.8171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2357.277 | 0.1112% | 63.7121 | 59.3999 | 55.1249 | 50.9103 | 46.7791 | 42.7536 | 38.8552 | 35.1039 | 31.5181 | 28.1141 | 775.6932 | 682.2283 | 595.4833 | 515.6327 | 442.756 | 376.8379 | 317.771 | 299.9723 | 291.0493 | 282.3918 | 273.9917 | 265.8416 | 257.9339 | 250.2614 | 242.8171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter data acquisition card/board (also called system input module); diagnose with fault code | Corrective | Repair | Inverter | 1 | 1 | 0 | Inverter | inverter | Inverter specialist | 33.1731 | 20 | 1 | Weibull | 10 | 1 | 0.5 | 1000 | 331.7308 | 10000 | 10331.7308 |  |  | 169.4072 | 1554.1577 | 0.0733% | 16.0932 | 15.6144 | 15.15 | 14.6993 | 14.2621 | 13.8378 | 13.4262 | 13.0268 | 12.6394 | 12.2634 | 370.5809 | 359.5576 | 348.8622 | 338.4849 | 328.4164 | 318.6473 | 309.1688 | 299.9723 | 291.0493 | 282.3918 | 273.9917 | 265.8416 | 257.9339 | 250.2614 | 242.8171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2357.277 | 0.1112% | 63.7121 | 59.3999 | 55.1249 | 50.9103 | 46.7791 | 42.7536 | 38.8552 | 35.1039 | 31.5181 | 28.1141 | 775.6932 | 682.2283 | 595.4833 | 515.6327 | 442.756 | 376.8379 | 317.771 | 299.9723 | 291.0493 | 282.3918 | 273.9917 | 265.8416 | 257.9339 | 250.2614 | 242.8171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace inverter relay/switch | Corrective | Repair | Inverter | 1 | 1 | 0 | Inverter | inverter | Inverter specialist | 33.1731 | 20 | 1 | Weibull | 10 | 1 | 0.5 | 55 | 331.7308 | 550 | 881.7308 |  |  | 20.9065 | 224.7419 | 0.0106% | 16.0932 | 15.6144 | 15.15 | 14.6993 | 14.2621 | 13.8378 | 13.4262 | 13.0268 | 12.6394 | 12.2634 | 31.6261 | 30.6854 | 29.7726 | 28.887 | 28.0277 | 27.194 | 26.3851 | 25.6002 | 24.8387 | 24.0999 | 23.383 | 22.6875 | 22.0126 | 21.3578 | 20.7225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 505.9099 | 0.02386% | 63.7121 | 59.3999 | 55.1249 | 50.9103 | 46.7791 | 42.7536 | 38.8552 | 35.1039 | 31.5181 | 28.1141 | 66.1992 | 58.2227 | 50.8197 | 44.0051 | 37.7857 | 32.1601 | 27.1192 | 25.6002 | 24.8387 | 24.0999 | 23.383 | 22.6875 | 22.0126 | 21.3578 | 20.7225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace maximum power point tracker card/board; diagnose with fault code | Corrective | Repair | Inverter | 1 | 1 | 0 | Inverter | inverter | Inverter specialist | 33.1731 | 20 | 1 | Weibull | 10 | 1 | 0.5 | 1000 | 331.7308 | 10000 | 10331.7308 |  |  | 169.4072 | 1554.1577 | 0.0733% | 16.0932 | 15.6144 | 15.15 | 14.6993 | 14.2621 | 13.8378 | 13.4262 | 13.0268 | 12.6394 | 12.2634 | 370.5809 | 359.5576 | 348.8622 | 338.4849 | 328.4164 | 318.6473 | 309.1688 | 299.9723 | 291.0493 | 282.3918 | 273.9917 | 265.8416 | 257.9339 | 250.2614 | 242.8171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2357.277 | 0.1112% | 63.7121 | 59.3999 | 55.1249 | 50.9103 | 46.7791 | 42.7536 | 38.8552 | 35.1039 | 31.5181 | 28.1141 | 775.6932 | 682.2283 | 595.4833 | 515.6327 | 442.756 | 376.8379 | 317.771 | 299.9723 | 291.0493 | 282.3918 | 273.9917 | 265.8416 | 257.9339 | 250.2614 | 242.8171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace overvoltage surge suppressors for inverter | Corrective | Repair | Inverter | 1 | 1 | 0 | Inverter | inverter | Inverter specialist | 33.1731 | 20 | 1 | Weibull | 10 | 1 | 0.5 | 25 | 331.7308 | 250 | 581.7308 |  |  | 16.1922 | 182.5382 | 0.008609% | 16.0932 | 15.6144 | 15.15 | 14.6993 | 14.2621 | 13.8378 | 13.4262 | 13.0268 | 12.6394 | 12.2634 | 20.8657 | 20.245 | 19.6428 | 19.0585 | 18.4916 | 17.9415 | 17.4078 | 16.89 | 16.3876 | 15.9001 | 15.4272 | 14.9683 | 14.523 | 14.091 | 13.6719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 447.1364 | 0.02109% | 63.7121 | 59.3999 | 55.1249 | 50.9103 | 46.7791 | 42.7536 | 38.8552 | 35.1039 | 31.5181 | 28.1141 | 43.6756 | 38.413 | 33.5288 | 29.0328 | 24.9295 | 21.218 | 17.8922 | 16.89 | 16.3876 | 15.9001 | 15.4272 | 14.9683 | 14.523 | 14.091 | 13.6719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace terminal block | Corrective |  | Inverter | 1 | 1 | 0 | Inverter | Combiner Box | Journeyman electrician | 19.9038 | 5 | 3 | Interval | 157 | 0.25 | 7.85 | 10 | 781.226 | 1570 | 2351.226 |  |  | 423.6543 | 3859.6148 | 0.182% | 0 | 0 | 0 | 0 | 862.5366 | 0 | 0 | 0 | 0 | 952.3101 | 0 | 0 | 0 | 0 | 3164.4406 | 0 | 0 | 0 | 0 | 3493.7981 | 0 | 0 | 0 | 0 | 3857.4354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3859.6148 | 0.182% | 0 | 0 | 0 | 0 | 862.5366 | 0 | 0 | 0 | 0 | 952.3101 | 0 | 0 | 0 | 0 | 3164.4406 | 0 | 0 | 0 | 0 | 3493.7981 | 0 | 0 | 0 | 0 | 3857.4354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Restore lost internet connection | Corrective | Repair | Monitoring | 1 | 0 | 0 | N/A | Site | Network/IT | 45.885 | 20 | 3 | Interval | 1 | 1 | 0.05 | 0 | 45.885 | 0 | 45.885 |  |  | 3.4091 | 17.6197 | 0.000831% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.1827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.6197 | 0.000831% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.1827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dispatch contractor in response to alarms, alerts, or contact by others | Corrective | Emergency Response | Whole System | 1 | 1 | 1 | Monitoring |  | Administrator | 22.9956 | 5 | 2 | Interval | 1 | 1 | 0.2 | 4 | 22.9956 | 4 | 26.9956 |  |  | 6.958 | 69.6743 | 0.003286% | 0 | 0 | 0 | 0 | 29.8053 | 0 | 0 | 0 | 0 | 32.9075 | 0 | 0 | 0 | 0 | 36.3325 | 0 | 0 | 0 | 0 | 40.114 | 0 | 0 | 0 | 0 | 44.2891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.6743 | 0.003286% | 0 | 0 | 0 | 0 | 29.8053 | 0 | 0 | 0 | 0 | 32.9075 | 0 | 0 | 0 | 0 | 36.3325 | 0 | 0 | 0 | 0 | 40.114 | 0 | 0 | 0 | 0 | 44.2891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair or replace rack parts damaged by corrosion or physical damage | Corrective | Repair | Rack | 1 | 1 | 1 | EPC |  | Mechanic | 29.2985 | 60 | 3 | Weibull | 163.9344 | 1 | 2.7322 | 200 | 4803.0265 | 32786.8852 | 37589.9117 |  |  | 99.7588 | 1151.3776 | 0.0543% | 0 | 2.1726 | 4.9857 | 9.0392 | 14.4022 | 21.145 | 29.3391 | 39.0563 | 50.3686 | 63.3476 | 78.0638 | 94.5865 | 112.9823 | 133.3153 | 155.646 | 180.0305 | 206.5197 | 235.1587 | 265.9858 | 299.0317 | 334.3187 | 371.8595 | 411.6567 | 453.7019 | 497.9745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1151.3776 | 0.0543% | 0 | 2.1726 | 4.9857 | 9.0392 | 14.4022 | 21.145 | 29.3391 | 39.0563 | 50.3686 | 63.3476 | 78.0638 | 94.5865 | 112.9823 | 133.3153 | 155.646 | 180.0305 | 206.5197 | 235.1587 | 265.9858 | 299.0317 | 334.3187 | 371.8595 | 411.6567 | 453.7019 | 497.9745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Excavate and replace failed foundation element | Corrective | Repair | Rack | 1 | 1 | 1 | N/A |  | Structural engineer | 55.8237 | 100 | 3 | Weibull | 16.3934 | 4 | 0.65574 | 400 | 3660.5675 | 6557.377 | 10217.9445 |  |  | 5.9545 | 69.3909 | 0.003273% | 0.031267 | 0.12757 | 0.29276 | 0.53086 | 0.846 | 1.2425 | 1.7248 | 2.2974 | 2.9652 | 3.733 | 4.6057 | 5.5885 | 6.6868 | 7.9059 | 9.2513 | 10.7287 | 12.3439 | 14.1026 | 16.0109 | 18.0748 | 20.3004 | 22.6939 | 25.2616 | 28.0097 | 30.9445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69.3909 | 0.003273% | 0.031267 | 0.12757 | 0.29276 | 0.53086 | 0.846 | 1.2425 | 1.7248 | 2.2974 | 2.9652 | 3.733 | 4.6057 | 5.5885 | 6.6868 | 7.9059 | 9.2513 | 10.7287 | 12.3439 | 14.1026 | 16.0109 | 18.0748 | 20.3004 | 22.6939 | 25.2616 | 28.0097 | 30.9445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace modules failing performance test or IR scan | Corrective | Repair | PV module | 1 | 1 | 0 | Module (Product) | modules | Journeyman electrician | 19.9038 | 25 | 2 | Weibull | 32787 | 0.15 | 196.722 | 244 | 97888.1106 | 8000028 | 8097916.1106 |  |  | 3096.718 | 452400.9101 | 21.34% | 318.996 | 647.6357 | 982.9872 | 1321.9732 | 1661.4184 | 1998.0983 | 2328.7908 | 2650.3274 | 2959.6436 | 3253.8275 | 3530.1657 | 3786.1846 | 4019.6874 | 4228.7851 | 4411.9212 | 4567.89 | 4695.8476 | 4795.3163 | 4866.1814 | 4908.6819 | 407293.9575 | 406286.1937 | 403151.4153 | 398008.9345 | 390996.6825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1097822.1263 | 51.78% | 318.996 | 647.6357 | 982.9872 | 1321.9732 | 1661.4184 | 1998.0983 | 2328.7908 | 3378.1645 | 4709.6754 | 6094.8534 | 7465.1064 | 8765.5191 | 9953.6838 | 10997.736 | 11874.4073 | 12567.4038 | 13066.1842 | 13365.1144 | 13462.9388 | 13362.5041 | 1081286.9591 | 1042210.0995 | 989438.6464 | 924555.0927 | 849480.8715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair or replace damage to module frame | Corrective | Repair | PV module | 1 | 1 | 0 | Module (Product) | modules | Mechanic | 29.2985 | 60 | 2 | Weibull | 32787 | 0.25 | 136.6125 | 50 | 240152.1646 | 1639350 | 1879502.1646 |  |  | 1735.5883 | 48657.4719 | 2.295% | 136.0484 | 277.3076 | 423.6918 | 575.1015 | 731.4235 | 892.5311 | 1058.2835 | 1228.5266 | 1403.0929 | 1581.8015 | 1764.4585 | 1950.8574 | 2140.7792 | 2333.9928 | 2530.2558 | 2729.3144 | 2930.9044 | 3134.7513 | 3340.5716 | 3548.0725 | 29403.0345 | 31046.1895 | 32695.2717 | 34347.772 | 36001.1422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48657.4719 | 2.295% | 136.0484 | 277.3076 | 423.6918 | 575.1015 | 731.4235 | 892.5311 | 1058.2835 | 1228.5266 | 1403.0929 | 1581.8015 | 1764.4585 | 1950.8574 | 2140.7792 | 2333.9928 | 2530.2558 | 2729.3144 | 2930.9044 | 3134.7513 | 3340.5716 | 3548.0725 | 29403.0345 | 31046.1895 | 32695.2717 | 34347.772 | 36001.1422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair cracking of PV module back sheet | Corrective | Repair | PV module | 1 | 1 | 0 | Module (Product) | modules | Journeyman electrician | 19.9038 | 50 | 3 | Weibull | 32787 | 0.1 | 65.574 | 25 | 65258.7404 | 819675 | 884933.7404 |  |  | 294.9016 | 19012.4904 | 0.8967% | 1.5975 | 6.5175 | 14.9554 | 27.1112 | 43.1873 | 63.3874 | 87.9135 | 116.9641 | 150.7314 | 189.3988 | 233.1379 | 282.105 | 336.4385 | 396.255 | 461.646 | 532.6742 | 609.3702 | 691.7284 | 779.704 | 873.2096 | 13182.2087 | 14594.0623 | 16073.451 | 17616.4788 | 19218.5004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19012.4904 | 0.8967% | 1.5975 | 6.5175 | 14.9554 | 27.1112 | 43.1873 | 63.3874 | 87.9135 | 116.9641 | 150.7314 | 189.3988 | 233.1379 | 282.105 | 336.4385 | 396.255 | 461.646 | 532.6742 | 609.3702 | 691.7284 | 779.704 | 873.2096 | 13182.2087 | 14594.0623 | 16073.451 | 17616.4788 | 19218.5004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair roof leaks | Corrective | Repair | Roof | 0 | 0 | 0 | N/A | m2 | Roofing | 22.7037 | 50 | 5 | Weibull | 0 | 1 | 0 | 25 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-roof (new roof) | Corrective | Repair | Roof | 0 | 1 | 0 | N/A | m2 | Roofing | 22.7037 | 50 | 10 | Weibull | 0 | 1 | 0 | 25 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair Roof Attachment Flashing | Corrective | Repair | Roof | 0 | 0 | 0 | N/A | each | Roofing | 22.7037 | 30 | 4 | Weibull | 31250 | 0.5 | 520.8333 | 25 | 354744.5913 | 781250 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace tracking controller power supply fan filter | Corrective | Repair | Tracker | 0 | 1 | 1 | EPC | Controller | Mechanic | 29.2985 | 2 | 1 | interval | 0 | 0.16667 | 0 | 25 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repair/replace tracker drive shaft | Corrective | Repair | Tracker | 0 | 1 | 1 | N/A | row | Mechanic | 29.2985 | 25 | 3 | Weibull | 0 | 0.5 | 0 | 120 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace hydraulic cylinder | Corrective | Repair | Tracker | 0 | 1 | 1 | N/A |  | Mechanic | 29.2985 | 25 | 3 | Weibull | 0 | 0.5 | 0 | 120 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace tracker drive bearing | Corrective | Repair | Tracker | 0 | 1 | 1 | N/A | row | Mechanic | 29.2985 | 25 | 3 | Weibull | 0 | 0.5 | 0 | 40 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace tracker motor controller | Corrective | Repair | Tracker | 0 | 1 | 1 | N/A |  | Journeyman electrician | 19.9038 | 25 | 3 | Weibull | 0 | 0.5 | 0 | 250 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace tracker mount bearing | Corrective | Repair | Tracker | 0 | 1 | 1 | N/A |  | Mechanic | 29.2985 | 25 | 3 | Weibull | 0 | 0.5 | 0 | 40 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace/upgrade tracker control software | Corrective | Repair | Tracker | 0 | 1 | 1 | N/A |  | Network/IT | 45.885 | 25 | 3 | Weibull | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace transformer | Corrective | Repair | Transformer | 1 | 0 | 0 | N/A | Transformer | Master electrician | 32.012 | 40 | 3 | Weibull | 10 | 4 | 1 | 50000 | 1280.4808 | 500000 | 501280.4808 |  |  | 4278.0964 | 48052.4867 | 2.266% | 23.9671 | 97.7751 | 224.3272 | 406.5448 | 647.3136 | 949.4232 | 1315.5029 | 1747.9502 | 2248.8566 | 2819.9275 | 3462.401 | 4176.9635 | 4963.6654 | 5821.8388 | 6750.0178 | 7745.8653 | 8806.1068 | 9926.4759 | 11101.6719 | 12325.3338 | 13590.0327 | 14887.2839 | 16207.5826 | 17540.4638 | 18874.5871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49211.0932 | 2.321% | 23.9671 | 97.7751 | 224.3272 | 406.5448 | 647.3136 | 949.4232 | 1315.5029 | 1747.9502 | 2248.8566 | 2819.9275 | 3462.401 | 4176.9635 | 4963.6654 | 5821.8388 | 6750.0178 | 7745.8653 | 8806.1068 | 9926.4759 | 11101.6719 | 12325.3338 | 13590.0327 | 14887.2839 | 16207.5826 | 18973.2194 | 23629.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-tap transformer | Corrective | Repair | Transformer | 1 | 0 | 0 | N/A | Transformer | Master electrician | 32.012 | 25 | 3 | Weibull | 10 | 2 | 0.8 | 0 | 640.2404 | 0 | 640.2404 |  |  | 18.23 | 185.8387 | 0.008765% | 0.12538 | 0.51131 | 1.172 | 2.1202 | 3.366 | 4.9152 | 6.7687 | 8.9206 | 11.3571 | 14.0557 | 16.9839 | 20.0992 | 23.349 | 26.6707 | 29.9931 | 33.2383 | 36.3236 | 39.1645 | 41.6783 | 43.7874 | 45.4233 | 46.5301 | 47.0678 | 47.0148 | 46.3697 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 523.28 | 0.02468% | 0.12538 | 0.51131 | 1.172 | 2.1202 | 3.366 | 4.9152 | 6.7687 | 8.9206 | 11.3571 | 14.0557 | 17.3716 | 30.3975 | 46.7589 | 65.4561 | 85.3513 | 105.3438 | 124.4564 | 141.8631 | 156.8824 | 168.9588 | 177.6427 | 182.5768 | 183.4914 | 180.2139 | 172.6906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check position of disconnect switches and breakers. | Preventive | Inspection | AC Wiring | 1 | 0 | 0 | N/A | Disconnect Box | Inspector | 33.12 | 1 | 1 | interval | 157 | 0.08 | 12.56 | 0 | 415.9872 | 0 | 415.9872 |  |  | 515.4771 | 5920.9462 | 0.2793% | 424.3069 | 432.7931 | 441.4489 | 450.2779 | 459.2835 | 468.4692 | 477.8385 | 487.3953 | 497.1432 | 507.0861 | 517.2278 | 527.5724 | 538.1238 | 548.8863 | 559.864 | 571.0613 | 582.4825 | 594.1322 | 606.0148 | 618.1351 | 630.4978 | 643.1078 | 655.9699 | 669.0893 | 682.4711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5920.9462 | 0.2793% | 424.3069 | 432.7931 | 441.4489 | 450.2779 | 459.2835 | 468.4692 | 477.8385 | 487.3953 | 497.1432 | 507.0861 | 517.2278 | 527.5724 | 538.1238 | 548.8863 | 559.864 | 571.0613 | 582.4825 | 594.1322 | 606.0148 | 618.1351 | 630.4978 | 643.1078 | 655.9699 | 669.0893 | 682.4711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inspect electrical boxes for corrosion or intrusion of water or insects. Seal boxes if required. | Preventive | Inspection | AC Wiring | 1 | 0 | 0 | N/A | Combiner Box | Inspector | 33.12 | 1 | 1 | interval | 157 | 0.08 | 12.56 | 0 | 415.9872 | 0 | 415.9872 |  |  | 515.4771 | 5920.9462 | 0.2793% | 424.3069 | 432.7931 | 441.4489 | 450.2779 | 459.2835 | 468.4692 | 477.8385 | 487.3953 | 497.1432 | 507.0861 | 517.2278 | 527.5724 | 538.1238 | 548.8863 | 559.864 | 571.0613 | 582.4825 | 594.1322 | 606.0148 | 618.1351 | 630.4978 | 643.1078 | 655.9699 | 669.0893 | 682.4711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5920.9462 | 0.2793% | 424.3069 | 432.7931 | 441.4489 | 450.2779 | 459.2835 | 468.4692 | 477.8385 | 487.3953 | 497.1432 | 507.0861 | 517.2278 | 527.5724 | 538.1238 | 548.8863 | 559.864 | 571.0613 | 582.4825 | 594.1322 | 606.0148 | 618.1351 | 630.4978 | 643.1078 | 655.9699 | 669.0893 | 682.4711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-torque all electrical connections on AC side of system. | Preventive | Service | AC Wiring | 1 | 0 | 0 | N/A |  | Journeyman electrician | 19.9038 | 5 | 1 | interval | 1 | 0.5 | 0.1 | 0 | 9.9519 | 0 | 9.9519 |  |  | 2.5651 | 25.6854 | 0.001211% | 0 | 0 | 0 | 0 | 10.9877 | 0 | 0 | 0 | 0 | 12.1313 | 0 | 0 | 0 | 0 | 13.394 | 0 | 0 | 0 | 0 | 14.788 | 0 | 0 | 0 | 0 | 16.3272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.6854 | 0.001211% | 0 | 0 | 0 | 0 | 10.9877 | 0 | 0 | 0 | 0 | 12.1313 | 0 | 0 | 0 | 0 | 13.394 | 0 | 0 | 0 | 0 | 14.788 | 0 | 0 | 0 | 0 | 16.3272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Exercise operation of all protection devices. | Preventive | Inspection | AC Wiring | 1 | 0 | 0 | N/A |  | Journeyman electrician | 19.9038 | 1 | 1 | interval | 2 | 0.08 | 0.16 | 0 | 3.1846 | 0 | 3.1846 |  |  | 3.9463 | 45.3282 | 0.002138% | 3.2483 | 3.3133 | 3.3795 | 3.4471 | 3.5161 | 3.5864 | 3.6581 | 3.7313 | 3.8059 | 3.882 | 3.9597 | 4.0389 | 4.1196 | 4.202 | 4.2861 | 4.3718 | 4.4592 | 4.5484 | 4.6394 | 4.7322 | 4.8268 | 4.9234 | 5.0218 | 5.1223 | 5.2247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.3282 | 0.002138% | 3.2483 | 3.3133 | 3.3795 | 3.4471 | 3.5161 | 3.5864 | 3.6581 | 3.7313 | 3.8059 | 3.882 | 3.9597 | 4.0389 | 4.1196 | 4.202 | 4.2861 | 4.3718 | 4.4592 | 4.5484 | 4.6394 | 4.7322 | 4.8268 | 4.9234 | 5.0218 | 5.1223 | 5.2247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monitoring annual service package | Preventive | Management | Asset Management | 1 | 1 | 1 | Monitoring | System | Administrator | 22.9956 | 1 | 1 | interval | 1 | 1 | 1 | 50 | 22.9956 | 50 | 72.9956 |  |  | 90.4536 | 1038.9812 | 0.049% | 74.4555 | 75.9446 | 77.4635 | 79.0128 | 80.593 | 82.2049 | 83.849 | 85.526 | 87.2365 | 88.9812 | 90.7608 | 92.576 | 94.4276 | 96.3161 | 98.2424 | 100.2073 | 102.2114 | 104.2557 | 106.3408 | 108.4676 | 110.6369 | 112.8497 | 115.1067 | 117.4088 | 119.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1038.9812 | 0.049% | 74.4555 | 75.9446 | 77.4635 | 79.0128 | 80.593 | 82.2049 | 83.849 | 85.526 | 87.2365 | 88.9812 | 90.7608 | 92.576 | 94.4276 | 96.3161 | 98.2424 | 100.2073 | 102.2114 | 104.2557 | 106.3408 | 108.4676 | 110.6369 | 112.8497 | 115.1067 | 117.4088 | 119.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Daily Operations and Performance Monitoring | Preventive | Management | Asset Management | 1 | 0 | 0 | N/A |  | Administrator | 22.9956 | 0.083333 | 1 | interval | 1 | 1 | 12 | 0 | 22.9956 | 0 | 22.9956 |  |  | 341.944 | 3927.6855 | 0.1852% | 281.4659 | 287.0952 | 292.8371 | 298.6938 | 304.6677 | 310.7611 | 316.9763 | 323.3158 | 329.7821 | 336.3778 | 343.1053 | 349.9674 | 356.9668 | 364.1061 | 371.3882 | 378.816 | 386.3923 | 394.1202 | 402.0026 | 410.0426 | 418.2435 | 426.6083 | 435.1405 | 443.8433 | 452.7202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3927.6855 | 0.1852% | 281.4659 | 287.0952 | 292.8371 | 298.6938 | 304.6677 | 310.7611 | 316.9763 | 323.3158 | 329.7821 | 336.3778 | 343.1053 | 349.9674 | 356.9668 | 364.1061 | 371.3882 | 378.816 | 386.3923 | 394.1202 | 402.0026 | 410.0426 | 418.2435 | 426.6083 | 435.1405 | 443.8433 | 452.7202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monitor alarms and site-specific altert parameters | Preventive | Management | Asset Management | 1 | 0 | 0 | N/A |  | Administrator | 22.9956 | 0.083333 | 1 | interval | 1 | 1 | 12 | 0 | 22.9956 | 0 | 22.9956 |  |  | 341.944 | 3927.6855 | 0.1852% | 281.4659 | 287.0952 | 292.8371 | 298.6938 | 304.6677 | 310.7611 | 316.9763 | 323.3158 | 329.7821 | 336.3778 | 343.1053 | 349.9674 | 356.9668 | 364.1061 | 371.3882 | 378.816 | 386.3923 | 394.1202 | 402.0026 | 410.0426 | 418.2435 | 426.6083 | 435.1405 | 443.8433 | 452.7202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3927.6855 | 0.1852% | 281.4659 | 287.0952 | 292.8371 | 298.6938 | 304.6677 | 310.7611 | 316.9763 | 323.3158 | 329.7821 | 336.3778 | 343.1053 | 349.9674 | 356.9668 | 364.1061 | 371.3882 | 378.816 | 386.3923 | 394.1202 | 402.0026 | 410.0426 | 418.2435 | 426.6083 | 435.1405 | 443.8433 | 452.7202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Array cleaning | Preventive | Cleaning | PV Module | 1 | 0 | 0 | N/A | m2 | Cleaner | 14.7355 | 1 | 1 | interval | 62500 | 0.02 | 1250 | 0.0112 | 18419.351 | 700 | 19119.351 | 2 gal fuel/acre @$4/gal + 500 gal H2O/acre @$0.40/gal |  | 23692.047 | 272134.9335 | 12.84% | 19501.738 | 19891.7727 | 20289.6082 | 20695.4004 | 21109.3084 | 21531.4945 | 21962.1244 | 22401.3669 | 22849.3943 | 23306.3821 | 23772.5098 | 24247.96 | 24732.9192 | 25227.5776 | 25732.1291 | 26246.7717 | 26771.7071 | 27307.1413 | 27853.2841 | 28410.3498 | 28978.5568 | 29558.1279 | 30149.2905 | 30752.2763 | 31367.3218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 272134.9335 | 12.84% | 19501.738 | 19891.7727 | 20289.6082 | 20695.4004 | 21109.3084 | 21531.4945 | 21962.1244 | 22401.3669 | 22849.3943 | 23306.3821 | 23772.5098 | 24247.96 | 24732.9192 | 25227.5776 | 25732.1291 | 26246.7717 | 26771.7071 | 27307.1413 | 27853.2841 | 28410.3498 | 28978.5568 | 29558.1279 | 30149.2905 | 30752.2763 | 31367.3218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
General Cleaning/Veg Mobilization | Preventive | Cleaning | PV Module | 1 | 0 | 0 | N/A | Site | Mower/Trimmer | 29.2985 | 0.5 | 1 | interval | 1 | 4 | 8 | 0 | 117.1938 | 0 | 117.1938 | Other cost = water truckr rental |  | 290.4452 | 3336.1529 | 0.1573% | 239.0754 | 243.857 | 248.7341 | 253.7088 | 258.783 | 263.9586 | 269.2378 | 274.6225 | 280.115 | 285.7173 | 291.4316 | 297.2603 | 303.2055 | 309.2696 | 315.455 | 321.7641 | 328.1994 | 334.7633 | 341.4586 | 348.2878 | 355.2535 | 362.3586 | 369.6058 | 376.9979 | 384.5379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3336.1529 | 0.1573% | 239.0754 | 243.857 | 248.7341 | 253.7088 | 258.783 | 263.9586 | 269.2378 | 274.6225 | 280.115 | 285.7173 | 291.4316 | 297.2603 | 303.2055 | 309.2696 | 315.455 | 321.7641 | 328.1994 | 334.7633 | 341.4586 | 348.2878 | 355.2535 | 362.3586 | 369.6058 | 376.9979 | 384.5379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vegetation management (mowing, trimming) per acre | Preventive | Cleaning | PV Module | 1 | 0 | 0 | N/A | Acre | Mower/Trimmer | 29.2985 | 0.25 | 1 | interval | 52.62 | 2 | 420.9598 | 0 | 3083.3683 | 0 | 3083.3683 | Other cost = 1 gal fuel/acre @ $4/gal + $10/acre mowing consumables |  | 15283.2191 | 175548.2686 | 8.28% | 12580.1429 | 12831.7457 | 13088.3806 | 13350.1482 | 13617.1512 | 13889.4942 | 14167.2841 | 14450.6298 | 14739.6424 | 15034.4352 | 15335.1239 | 15641.8264 | 15954.6629 | 16273.7562 | 16599.2313 | 16931.216 | 17269.8403 | 17615.2371 | 17967.5418 | 18326.8927 | 18693.4305 | 19067.2991 | 19448.6451 | 19837.618 | 20234.3704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175548.2686 | 8.28% | 12580.1429 | 12831.7457 | 13088.3806 | 13350.1482 | 13617.1512 | 13889.4942 | 14167.2841 | 14450.6298 | 14739.6424 | 15034.4352 | 15335.1239 | 15641.8264 | 15954.6629 | 16273.7562 | 16599.2313 | 16931.216 | 17269.8403 | 17615.2371 | 17967.5418 | 18326.8927 | 18693.4305 | 19067.2991 | 19448.6451 | 19837.618 | 20234.3704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bird Cleaning | Preventive | Cleaning | PV Module | 0 | 0 | 0 | N/A | acres | Cleaner | 14.7355 | 0.5 | 1 | interval | 1 | 4 | 8 | 120 | 58.9419 | 120 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Snow Removal | Preventive | Cleaning | PV Module | 0 | 0 | 0 | N/A | acres | Mower/Trimmer | 29.2985 | 0.5 | 1 | interval | 1 | 2 | 4 | 100 | 58.5969 | 100 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pollen Cleaning | Preventive | Cleaning | PV Module | 0 | 0 | 0 | N/A | acres | Cleaner | 14.7355 | 1 | 1 | interval | 1 | 4 | 4 | 120 | 58.9419 | 120 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dust Removal | Preventive | Cleaning | PV Module | 0 | 0 | 0 | N/A | acres | Cleaner | 14.7355 | 1 | 1 | interval | 1 | 4 | 4 | 120 | 58.9419 | 120 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check proper position of DC disconnect switches. | Preventive | Inspection | DC Wiring | 1 | 0 | 0 | N/A |  | Inspector | 33.12 | 1 | 1 | interval | 157 | 0.08 | 12.56 | 0 | 415.9872 | 0 | 415.9872 |  |  | 515.4771 | 5920.9462 | 0.2793% | 424.3069 | 432.7931 | 441.4489 | 450.2779 | 459.2835 | 468.4692 | 477.8385 | 487.3953 | 497.1432 | 507.0861 | 517.2278 | 527.5724 | 538.1238 | 548.8863 | 559.864 | 571.0613 | 582.4825 | 594.1322 | 606.0148 | 618.1351 | 630.4978 | 643.1078 | 655.9699 | 669.0893 | 682.4711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5920.9462 | 0.2793% | 424.3069 | 432.7931 | 441.4489 | 450.2779 | 459.2835 | 468.4692 | 477.8385 | 487.3953 | 497.1432 | 507.0861 | 517.2278 | 527.5724 | 538.1238 | 548.8863 | 559.864 | 571.0613 | 582.4825 | 594.1322 | 606.0148 | 618.1351 | 630.4978 | 643.1078 | 655.9699 | 669.0893 | 682.4711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inspect cabling for signs of cracks, defects, pulling out of connections; overheating, arcing, short or open circuits, ground faults in wiring and condition of wire insulation and protective materials.. | Preventive | Inspection | DC Wiring | 1 | 0 | 0 | N/A | strings | Inspector | 33.12 | 5 | 1 | interval | 2341.9204 | 0.05 | 23.4192 | 0 | 3878.2201 | 0 | 3878.2201 |  |  | 999.5901 | 10009.4972 | 0.4721% | 0 | 0 | 0 | 0 | 4281.8684 | 0 | 0 | 0 | 0 | 4727.5287 | 0 | 0 | 0 | 0 | 5219.5737 | 0 | 0 | 0 | 0 | 5762.8311 | 0 | 0 | 0 | 0 | 6362.6312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10009.4972 | 0.4721% | 0 | 0 | 0 | 0 | 4281.8684 | 0 | 0 | 0 | 0 | 4727.5287 | 0 | 0 | 0 | 0 | 5219.5737 | 0 | 0 | 0 | 0 | 5762.8311 | 0 | 0 | 0 | 0 | 6362.6312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Look for any signs of intrusion by pests such as insects and rodents. Remove any nests from electrical boxes (junction boxes, pull boxes, combiner boxes) or around the array. Use safe sanitation practices because pests may carry disease. | Preventive | Inspection | DC Wiring | 1 | 0 | 0 | N/A |  | Pest control | 20.1294 | 1 | 1 | interval | 324 | 0.15 | 48.6 | 1 | 978.29 | 324 | 1302.29 |  |  | 1613.7533 | 18536.1204 | 0.8743% | 1328.3358 | 1354.9025 | 1382.0005 | 1409.6405 | 1437.8333 | 1466.59 | 1495.9218 | 1525.8403 | 1556.3571 | 1587.4842 | 1619.2339 | 1651.6186 | 1684.6509 | 1718.3439 | 1752.7108 | 1787.765 | 1823.5203 | 1859.9908 | 1897.1906 | 1935.1344 | 1973.8371 | 2013.3138 | 2053.5801 | 2094.6517 | 2136.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18536.1204 | 0.8743% | 1328.3358 | 1354.9025 | 1382.0005 | 1409.6405 | 1437.8333 | 1466.59 | 1495.9218 | 1525.8403 | 1556.3571 | 1587.4842 | 1619.2339 | 1651.6186 | 1684.6509 | 1718.3439 | 1752.7108 | 1787.765 | 1823.5203 | 1859.9908 | 1897.1906 | 1935.1344 | 1973.8371 | 2013.3138 | 2053.5801 | 2094.6517 | 2136.5447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Open each combiner box and check that no fuses have blown and that all electrical connections are tight. Use an infrared camera for identifying loose connections because they are warmer than good connections when passing current. | Preventive | Inspection | DC Wiring | 1 | 0 | 0 | N/A | Combiner Box | Journeyman electrician | 19.9038 | 1 | 1 | interval | 157 | 0.15 | 23.55 | 0 | 468.7356 | 0 | 468.7356 |  |  | 580.8411 | 6671.7393 | 0.3147% | 478.1103 | 487.6725 | 497.4259 | 507.3745 | 517.522 | 527.8724 | 538.4298 | 549.1984 | 560.1824 | 571.3861 | 582.8138 | 594.47 | 606.3595 | 618.4866 | 630.8564 | 643.4735 | 656.343 | 669.4698 | 682.8592 | 696.5164 | 710.4467 | 724.6557 | 739.1488 | 753.9318 | 769.0104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6671.7393 | 0.3147% | 478.1103 | 487.6725 | 497.4259 | 507.3745 | 517.522 | 527.8724 | 538.4298 | 549.1984 | 560.1824 | 571.3861 | 582.8138 | 594.47 | 606.3595 | 618.4866 | 630.8564 | 643.4735 | 656.343 | 669.4698 | 682.8592 | 696.5164 | 710.4467 | 724.6557 | 739.1488 | 753.9318 | 769.0104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Re-torque all electrical connections in combiner box. | Preventive | Service | DC Wiring | 1 | 0 | 0 | N/A | Combiner Box | Journeyman electrician | 19.9038 | 1 | 1 | interval | 157 | 0.25 | 39.25 | 0 | 781.226 | 0 | 781.226 |  |  | 968.0685 | 11119.5655 | 0.5245% | 796.8505 | 812.7875 | 829.0432 | 845.6241 | 862.5366 | 879.7873 | 897.3831 | 915.3307 | 933.6373 | 952.3101 | 971.3563 | 990.7834 | 1010.5991 | 1030.8111 | 1051.4273 | 1072.4558 | 1093.9049 | 1115.783 | 1138.0987 | 1160.8607 | 1184.0779 | 1207.7595 | 1231.9146 | 1256.5529 | 1281.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11119.5655 | 0.5245% | 796.8505 | 812.7875 | 829.0432 | 845.6241 | 862.5366 | 879.7873 | 897.3831 | 915.3307 | 933.6373 | 952.3101 | 971.3563 | 990.7834 | 1010.5991 | 1030.8111 | 1051.4273 | 1072.4558 | 1093.9049 | 1115.783 | 1138.0987 | 1160.8607 | 1184.0779 | 1207.7595 | 1231.9146 | 1256.5529 | 1281.684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test system grounding with "megger" | Preventive | Inspection | DC Wiring | 1 | 0 | 0 | N/A | strings | Master electrician | 32.012 | 5 | 1 | interval | 1 | 0.25 | 0.05 | 0 | 8.003 | 0 | 8.003 |  |  | 2.0627 | 20.6554 | 0.0009742% | 0 | 0 | 0 | 0 | 8.836 | 0 | 0 | 0 | 0 | 9.7556 | 0 | 0 | 0 | 0 | 10.771 | 0 | 0 | 0 | 0 | 11.892 | 0 | 0 | 0 | 0 | 13.1298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.6554 | 0.0009742% | 0 | 0 | 0 | 0 | 8.836 | 0 | 0 | 0 | 0 | 9.7556 | 0 | 0 | 0 | 0 | 10.771 | 0 | 0 | 0 | 0 | 11.892 | 0 | 0 | 0 | 0 | 13.1298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inverter inspection | Preventive | Inspection | Electrical | 1 | 0 | 0 | N/A | Inverter | Inspector | 33.12 | 1 | 1 | interval | 10 | 0.5 | 5 | 0 | 165.6 | 0 | 165.6 |  |  | 205.2059 | 2357.0646 | 0.1112% | 168.912 | 172.2902 | 175.736 | 179.2508 | 182.8358 | 186.4925 | 190.2223 | 194.0268 | 197.9073 | 201.8655 | 205.9028 | 210.0208 | 214.2213 | 218.5057 | 222.8758 | 227.3333 | 231.88 | 236.5176 | 241.2479 | 246.0729 | 250.9943 | 256.0142 | 261.1345 | 266.3572 | 271.6844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2357.0646 | 0.1112% | 168.912 | 172.2902 | 175.736 | 179.2508 | 182.8358 | 186.4925 | 190.2223 | 194.0268 | 197.9073 | 201.8655 | 205.9028 | 210.0208 | 214.2213 | 218.5057 | 222.8758 | 227.3333 | 231.88 | 236.5176 | 241.2479 | 246.0729 | 250.9943 | 256.0142 | 261.1345 | 266.3572 | 271.6844 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Electrical labor mobilization | Preventive | Management | Electrical | 1 | 1 | 1 | EPC | Site | Master electrician | 32.012 | 1 | 1 | interval | 1 | 1 | 1 | 0 | 32.012 | 0 | 32.012 |  |  | 38.0356 | 425.1264 | 0.02005% | 0 | 33.3053 | 33.9714 | 34.6508 | 35.3439 | 36.0507 | 36.7717 | 37.5072 | 38.2573 | 39.0225 | 39.8029 | 40.599 | 41.411 | 42.2392 | 43.084 | 43.9456 | 44.8246 | 45.721 | 46.6355 | 47.5682 | 48.5195 | 49.4899 | 50.4797 | 51.4893 | 52.5191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 425.1264 | 0.02005% | 0 | 33.3053 | 33.9714 | 34.6508 | 35.3439 | 36.0507 | 36.7717 | 37.5072 | 38.2573 | 39.0225 | 39.8029 | 40.599 | 41.411 | 42.2392 | 43.084 | 43.9456 | 44.8246 | 45.721 | 46.6355 | 47.5682 | 48.5195 | 49.4899 | 50.4797 | 51.4893 | 52.5191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DC circuit test & combiner box inspection | Preventive | Testing | Electrical | 1 | 0 | 0 | N/A | Combiner Box | PV module/array Specialist | 33.1731 | 1 | 1 | interval | 157 | 0.083333 | 13.0833 | 0 | 434.0144 | 0 | 434.0144 |  |  | 537.8159 | 6177.5364 | 0.2914% | 442.6947 | 451.5486 | 460.5796 | 469.7912 | 479.187 | 488.7707 | 498.5461 | 508.5171 | 518.6874 | 529.0612 | 539.6424 | 550.4352 | 561.4439 | 572.6728 | 584.1263 | 595.8088 | 607.725 | 619.8795 | 632.2771 | 644.9226 | 657.8211 | 670.9775 | 684.397 | 698.085 | 712.0467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6177.5364 | 0.2914% | 442.6947 | 451.5486 | 460.5796 | 469.7912 | 479.187 | 488.7707 | 498.5461 | 508.5171 | 518.6874 | 529.0612 | 539.6424 | 550.4352 | 561.4439 | 572.6728 | 584.1263 | 595.8088 | 607.725 | 619.8795 | 632.2771 | 644.9226 | 657.8211 | 670.9775 | 684.397 | 698.085 | 712.0467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV module electrical connection check | Preventive | Testing | Electrical | 0 | 0 | 0 | N/A | PV Module | PV module/array Specialist | 33.1731 | 5 | 1 | Interval | 32786.8852 | 0.0041667 | 27.3224 | 0 | 4531.8411 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check grounding hardware | Preventive | Testing | Electrical | 1 | 0 | 0 | N/A | Structure | Master electrician | 32.012 | 1 | 1 | interval | 1 | 0.00055556 | 0.00055556 | 0 | 0.017784 | 0 | 0.017784 |  |  | 0.022038 | 0.25313 | 1.194e-05% | 0.01814 | 0.018503 | 0.018873 | 0.01925 | 0.019635 | 0.020028 | 0.020429 | 0.020837 | 0.021254 | 0.021679 | 0.022113 | 0.022555 | 0.023006 | 0.023466 | 0.023936 | 0.024414 | 0.024903 | 0.025401 | 0.025909 | 0.026427 | 0.026955 | 0.027494 | 0.028044 | 0.028605 | 0.029177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25313 | 1.194e-05% | 0.01814 | 0.018503 | 0.018873 | 0.01925 | 0.019635 | 0.020028 | 0.020429 | 0.020837 | 0.021254 | 0.021679 | 0.022113 | 0.022555 | 0.023006 | 0.023466 | 0.023936 | 0.024414 | 0.024903 | 0.025401 | 0.025909 | 0.026427 | 0.026955 | 0.027494 | 0.028044 | 0.028605 | 0.029177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Install software updates, inverter and other | Preventive | Service | Electrical | 1 | 1 | 1 | EPC | NCU | Inverter specialist | 33.1731 | 5 | 1 | interval | 10 | 0.5 | 1 | 0 | 165.8654 | 0 | 165.8654 |  |  | 42.7509 | 428.0905 | 0.02019% | 0 | 0 | 0 | 0 | 183.1288 | 0 | 0 | 0 | 0 | 202.189 | 0 | 0 | 0 | 0 | 223.233 | 0 | 0 | 0 | 0 | 246.4672 | 0 | 0 | 0 | 0 | 272.1197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 428.0905 | 0.02019% | 0 | 0 | 0 | 0 | 183.1288 | 0 | 0 | 0 | 0 | 202.189 | 0 | 0 | 0 | 0 | 223.233 | 0 | 0 | 0 | 0 | 246.4672 | 0 | 0 | 0 | 0 | 272.1197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check central SCADA/network manager | Preventive | Management | Electrical | 1 | 0 | 0 | N/A | NCU | Network/IT | 45.885 | 1 | 1 | interval | 1 | 0.25 | 0.25 | 0 | 11.4712 | 0 | 11.4712 |  |  | 14.2148 | 163.2758 | 0.007701% | 11.7007 | 11.9347 | 12.1734 | 12.4168 | 12.6652 | 12.9185 | 13.1769 | 13.4404 | 13.7092 | 13.9834 | 14.2631 | 14.5483 | 14.8393 | 15.1361 | 15.4388 | 15.7476 | 16.0625 | 16.3838 | 16.7114 | 17.0457 | 17.3866 | 17.7343 | 18.089 | 18.4508 | 18.8198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163.2758 | 0.007701% | 11.7007 | 11.9347 | 12.1734 | 12.4168 | 12.6652 | 12.9185 | 13.1769 | 13.4404 | 13.7092 | 13.9834 | 14.2631 | 14.5483 | 14.8393 | 15.1361 | 15.4388 | 15.7476 | 16.0625 | 16.3838 | 16.7114 | 17.0457 | 17.3866 | 17.7343 | 18.089 | 18.4508 | 18.8198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AC disconnect box inspection | Preventive | Inspection | Electrical | 1 | 0 | 0 | N/A | Disconnect Box | Inspector | 33.12 | 5 | 1 | interval | 1 | 0.25 | 0.05 | 0 | 8.28 | 0 | 8.28 |  |  | 2.1341 | 21.3703 | 0.001008% | 0 | 0 | 0 | 0 | 9.1418 | 0 | 0 | 0 | 0 | 10.0933 | 0 | 0 | 0 | 0 | 11.1438 | 0 | 0 | 0 | 0 | 12.3036 | 0 | 0 | 0 | 0 | 13.5842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.3703 | 0.001008% | 0 | 0 | 0 | 0 | 9.1418 | 0 | 0 | 0 | 0 | 10.0933 | 0 | 0 | 0 | 0 | 11.1438 | 0 | 0 | 0 | 0 | 12.3036 | 0 | 0 | 0 | 0 | 13.5842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Calibrate or replace weather sensors & meters | Preventive | Service | Electrical | 1 | 0 | 0 | N/A | Weather Station | Network/IT | 45.885 | 5 | 1 | interval | 1 | 0.5 | 0.1 | 500 | 22.9425 | 500 | 522.9425 |  |  | 134.7856 | 1349.6891 | 0.06366% | 0 | 0 | 0 | 0 | 577.3708 | 0 | 0 | 0 | 0 | 637.464 | 0 | 0 | 0 | 0 | 703.8118 | 0 | 0 | 0 | 0 | 777.065 | 0 | 0 | 0 | 0 | 857.9426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1349.6891 | 0.06366% | 0 | 0 | 0 | 0 | 577.3708 | 0 | 0 | 0 | 0 | 637.464 | 0 | 0 | 0 | 0 | 703.8118 | 0 | 0 | 0 | 0 | 777.065 | 0 | 0 | 0 | 0 | 857.9426 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Transformer/switchgear inspection | Preventive | Inspection | Electrical | 1 | 0 | 0 | N/A | Transformer | Inspector | 33.12 | 1 | 1 | interval | 10 | 2 | 20 | 0 | 662.4 | 0 | 662.4 |  |  | 820.8235 | 9428.2583 | 0.4447% | 675.648 | 689.161 | 702.9442 | 717.0031 | 731.3431 | 745.97 | 760.8894 | 776.1072 | 791.6293 | 807.4619 | 823.6111 | 840.0834 | 856.885 | 874.0227 | 891.5032 | 909.3333 | 927.5199 | 946.0703 | 964.9917 | 984.2916 | 1003.9774 | 1024.0569 | 1044.5381 | 1065.4288 | 1086.7374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9428.2583 | 0.4447% | 675.648 | 689.161 | 702.9442 | 717.0031 | 731.3431 | 745.97 | 760.8894 | 776.1072 | 791.6293 | 807.4619 | 823.6111 | 840.0834 | 856.885 | 874.0227 | 891.5032 | 909.3333 | 927.5199 | 946.0703 | 964.9917 | 984.2916 | 1003.9774 | 1024.0569 | 1044.5381 | 1065.4288 | 1086.7374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Clean (vacuum) dust from heat rejection fins | Preventive | Service | Inverter | 1 | 0 | 0 | N/A | inverter | Cleaner | 14.7355 | 1 | 1 | interval | 10 | 0.1 | 1 | 0 | 14.7355 | 0 | 14.7355 |  |  | 18.2597 | 209.7372 | 0.009892% | 15.0302 | 15.3308 | 15.6374 | 15.9502 | 16.2692 | 16.5945 | 16.9264 | 17.265 | 17.6103 | 17.9625 | 18.3217 | 18.6882 | 19.0619 | 19.4432 | 19.832 | 20.2287 | 20.6332 | 21.0459 | 21.4668 | 21.8961 | 22.3341 | 22.7808 | 23.2364 | 23.7011 | 24.1751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209.7372 | 0.009892% | 15.0302 | 15.3308 | 15.6374 | 15.9502 | 16.2692 | 16.5945 | 16.9264 | 17.265 | 17.6103 | 17.9625 | 18.3217 | 18.6882 | 19.0619 | 19.4432 | 19.832 | 20.2287 | 20.6332 | 21.0459 | 21.4668 | 21.8961 | 22.3341 | 22.7808 | 23.2364 | 23.7011 | 24.1751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Performance test: measure incident light while observing temp and energy output. Calculate PV module efficiency as a function of temp and calculate BOS efficiency. Compare readings with diagnostic benchmark (original efficiency of system). | Preventive | Testing | Inverter | 1 | 0 |  | N/A |  | Inspector | 33.12 | 1 | 1 | interval | 1 | 1 | 1 | 0 | 33.12 | 0 | 33.12 |  |  | 41.0412 | 471.4129 | 0.02223% | 33.7824 | 34.458 | 35.1472 | 35.8502 | 36.5672 | 37.2985 | 38.0445 | 38.8054 | 39.5815 | 40.3731 | 41.1806 | 42.0042 | 42.8443 | 43.7011 | 44.5752 | 45.4667 | 46.376 | 47.3035 | 48.2496 | 49.2146 | 50.1989 | 51.2028 | 52.2269 | 53.2714 | 54.3369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 471.4129 | 0.02223% | 33.7824 | 34.458 | 35.1472 | 35.8502 | 36.5672 | 37.2985 | 38.0445 | 38.8054 | 39.5815 | 40.3731 | 41.1806 | 42.0042 | 42.8443 | 43.7011 | 44.5752 | 45.4667 | 46.376 | 47.3035 | 48.2496 | 49.2146 | 50.1989 | 51.2028 | 52.2269 | 53.2714 | 54.3369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace any air filters on air-cooled equipment such as inverter. | Preventive | Service | Inverter | 1 | 0 | 0 | N/A | inverter | Inverter specialist | 33.1731 | 1 | 1 | interval | 10 | 0.25 | 2.5 | 25 | 82.9327 | 250 | 332.9327 |  |  | 412.5588 | 4738.7914 | 0.2235% | 339.5913 | 346.3832 | 353.3108 | 360.3771 | 367.5846 | 374.9363 | 382.435 | 390.0837 | 397.8854 | 405.8431 | 413.96 | 422.2392 | 430.6839 | 439.2976 | 448.0836 | 457.0452 | 466.1861 | 475.5099 | 485.0201 | 494.7205 | 504.6149 | 514.7072 | 525.0013 | 535.5013 | 546.2114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4738.7914 | 0.2235% | 339.5913 | 346.3832 | 353.3108 | 360.3771 | 367.5846 | 374.9363 | 382.435 | 390.0837 | 397.8854 | 405.8431 | 413.96 | 422.2392 | 430.6839 | 439.2976 | 448.0836 | 457.0452 | 466.1861 | 475.5099 | 485.0201 | 494.7205 | 504.6149 | 514.7072 | 525.0013 | 535.5013 | 546.2114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replace transient voltage surge suppression devices | Preventive | Service | Inverter | 1 | 0 | 0 | Inverter |  | Master electrician | 32.012 | 5 | 1 | interval | 10 | 0.5 | 1 | 105 | 160.0601 | 1050 | 1210.0601 |  |  | 311.8864 | 3123.1061 | 0.1473% | 0 | 0 | 0 | 0 | 1336.0041 | 0 | 0 | 0 | 0 | 1475.0565 | 0 | 0 | 0 | 0 | 1628.5816 | 0 | 0 | 0 | 0 | 1798.0856 | 0 | 0 | 0 | 0 | 1985.2318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3123.1061 | 0.1473% | 0 | 0 | 0 | 0 | 1336.0041 | 0 | 0 | 0 | 0 | 1475.0565 | 0 | 0 | 0 | 0 | 1628.5816 | 0 | 0 | 0 | 0 | 1798.0856 | 0 | 0 | 0 | 0 | 1985.2318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test overvoltage surge suppressors in inverter | Preventive | Testing | Inverter | 0 | 0 | 0 | Inverter | inverter | Inverter specialist | 33.1731 | 5 | 1 | interval | 10 | 0.1 | 0.2 | 0 | 33.1731 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV module torque check & visual inspection | Preventive | Inspection | Mechanical | 1 | 0 | 0 | N/A | Rail/ Fastener | PV module/array Specialist | 33.1731 | 5 | 1 | interval | 33114.7541 | 0.0083333 | 55.1913 | 0 | 9154.319 | 0 | 9154.319 |  |  | 2359.4758 | 23626.8514 | 1.114% | 0 | 0 | 0 | 0 | 10107.1079 | 0 | 0 | 0 | 0 | 11159.0638 | 0 | 0 | 0 | 0 | 12320.5082 | 0 | 0 | 0 | 0 | 13602.8365 | 0 | 0 | 0 | 0 | 15018.6307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23626.8514 | 1.114% | 0 | 0 | 0 | 0 | 10107.1079 | 0 | 0 | 0 | 0 | 11159.0638 | 0 | 0 | 0 | 0 | 12320.5082 | 0 | 0 | 0 | 0 | 13602.8365 | 0 | 0 | 0 | 0 | 15018.6307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Racking torque check & inspection | Preventive | Inspection | Mechanical | 1 | 0 | 0 | N/A | Structure | Inspector | 33.12 | 5 | 1 | interval | 1639.3443 | 0.0083333 | 2.7322 | 0 | 452.459 | 0 | 452.459 |  |  | 116.6188 | 1167.7747 | 0.05508% | 0 | 0 | 0 | 0 | 499.5513 | 0 | 0 | 0 | 0 | 551.545 | 0 | 0 | 0 | 0 | 608.9503 | 0 | 0 | 0 | 0 | 672.3303 | 0 | 0 | 0 | 0 | 742.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1167.7747 | 0.05508% | 0 | 0 | 0 | 0 | 499.5513 | 0 | 0 | 0 | 0 | 551.545 | 0 | 0 | 0 | 0 | 608.9503 | 0 | 0 | 0 | 0 | 672.3303 | 0 | 0 | 0 | 0 | 742.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Corrosion inspection | Preventive | Inspection | Mechanical | 1 | 0 | 0 | N/A | connection | Inspector | 33.12 | 5 | 1 | interval | 1639.3443 | 0.1 | 32.7869 | 0 | 5429.5082 | 0 | 5429.5082 |  |  | 1399.4261 | 14013.2961 | 0.6609% | 0 | 0 | 0 | 0 | 5994.6158 | 0 | 0 | 0 | 0 | 6618.5402 | 0 | 0 | 0 | 0 | 7307.4032 | 0 | 0 | 0 | 0 | 8067.9636 | 0 | 0 | 0 | 0 | 8907.6837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14013.2961 | 0.6609% | 0 | 0 | 0 | 0 | 5994.6158 | 0 | 0 | 0 | 0 | 6618.5402 | 0 | 0 | 0 | 0 | 7307.4032 | 0 | 0 | 0 | 0 | 8067.9636 | 0 | 0 | 0 | 0 | 8907.6837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Galvanazation inspection | Preventive | Inspection | Mechanical | 1 | 0 | 0 | N/A | connection | Inspector | 33.12 | 5 | 1 | interval | 1639.3443 | 0.1 | 32.7869 | 0 | 5429.5082 | 0 | 5429.5082 |  |  | 1399.4261 | 14013.2961 | 0.6609% | 0 | 0 | 0 | 0 | 5994.6158 | 0 | 0 | 0 | 0 | 6618.5402 | 0 | 0 | 0 | 0 | 7307.4032 | 0 | 0 | 0 | 0 | 8067.9636 | 0 | 0 | 0 | 0 | 8907.6837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14013.2961 | 0.6609% | 0 | 0 | 0 | 0 | 5994.6158 | 0 | 0 | 0 | 0 | 6618.5402 | 0 | 0 | 0 | 0 | 7307.4032 | 0 | 0 | 0 | 0 | 8067.9636 | 0 | 0 | 0 | 0 | 8907.6837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mechanical labor mobilization | Preventive | Management | Mechanical | 1 | 0 | 0 | EPC | Site | Mechanic | 29.2985 | 1 | 1 | interval | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Torque inspection | Preventive | Inspection | Mechanical | 1 | 0 | 0 | N/A | block | Inspector | 33.12 | 1 | 1 | interval | 10.2459 | 0.1 | 1.0246 | 0 | 33.9344 | 0 | 33.9344 |  |  | 42.0504 | 483.005 | 0.02278% | 34.6131 | 35.3054 | 36.0115 | 36.7317 | 37.4663 | 38.2157 | 38.98 | 39.7596 | 40.5548 | 41.3659 | 42.1932 | 43.0371 | 43.8978 | 44.7758 | 45.6713 | 46.5847 | 47.5164 | 48.4667 | 49.4361 | 50.4248 | 51.4333 | 52.4619 | 53.5112 | 54.5814 | 55.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483.005 | 0.02278% | 34.6131 | 35.3054 | 36.0115 | 36.7317 | 37.4663 | 38.2157 | 38.98 | 39.7596 | 40.5548 | 41.3659 | 42.1932 | 43.0371 | 43.8978 | 44.7758 | 45.6713 | 46.5847 | 47.5164 | 48.4667 | 49.4361 | 50.4248 | 51.4333 | 52.4619 | 53.5112 | 54.5814 | 55.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Spot-check monitoring instruments (pyranometer, etc) with hand-held instruments to ensure that they are operational and within specifications. | Preventive | Inspection | Monitoring | 0 | 0 | 0 | N/A |  | Inspector | 33.12 | 1 | 1 | interval | 1 | 1 | 1 | 0 | 33.12 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Contractor available by email and phone 24x7x365 | Preventive | Emergency Response | Whole System | 1 | 0 | 0 | N/A |  | Administrator | 22.9956 | 1 | 1 | interval | 1 | 1 | 1 | 0 | 22.9956 | 0 | 22.9956 |  |  | 28.4953 | 327.3071 | 0.01544% | 23.4555 | 23.9246 | 24.4031 | 24.8912 | 25.389 | 25.8968 | 26.4147 | 26.943 | 27.4818 | 28.0315 | 28.5921 | 29.164 | 29.7472 | 30.3422 | 30.949 | 31.568 | 32.1994 | 32.8433 | 33.5002 | 34.1702 | 34.8536 | 35.5507 | 36.2617 | 36.9869 | 37.7267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 327.3071 | 0.01544% | 23.4555 | 23.9246 | 24.4031 | 24.8912 | 25.389 | 25.8968 | 26.4147 | 26.943 | 27.4818 | 28.0315 | 28.5921 | 29.164 | 29.7472 | 30.3422 | 30.949 | 31.568 | 32.1994 | 32.8433 | 33.5002 | 34.1702 | 34.8536 | 35.5507 | 36.2617 | 36.9869 | 37.7267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test open circuit voltage or IV curve of series strings of modules | Preventive | Inspection | DC Wiring | 0 | 0 | 0 | N/A | strings | PV module/array Specialist | 33.1731 | 5 | 1 | interval | 2341.9204 | 0.15 | 70.2576 | 0 | 11653.3057 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inspect ballasted, non-penetrating mounting system for abnormal movement | Preventive | Inspection | Rack | 0 | 0 | 0 | N/A | rows | Inspector | 33.12 | 1 | 1 | interval | 0 | 0.08 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remove bird nests from array and rack area. | Preventive | Service | Rack | 0 | 0 | 0 | N/A | Acres | Pest control | 20.1294 | 1 | 1 | interval | 52.62 | 4 | 210.4799 | 0 | 4236.8386 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walk through each row of the PV array and check the PV modules for any damage. Report any damage to rack and damaged modules for warranty replacement. Note location and serial number of questionable modules. | Preventive | Inspection | PV Module | 1 | 0 | 0 | N/A | Acres | Inspector | 33.12 | 2 | 1 | interval | 52.62 | 0.5 | 13.155 | 0 | 871.3867 | 0 | 871.3867 |  |  | 545.2418 | 5924.523 | 0.2794% | 0 | 906.5907 | 0 | 943.217 | 0 | 981.323 | 0 | 1020.9684 | 0 | 1062.2155 | 0 | 1105.129 | 0 | 1149.7763 | 0 | 1196.2272 | 0 | 1244.5548 | 0 | 1294.8348 | 0 | 1347.1461 | 0 | 1401.5708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5924.523 | 0.2794% | 0 | 906.5907 | 0 | 943.217 | 0 | 981.323 | 0 | 1020.9684 | 0 | 1062.2155 | 0 | 1105.129 | 0 | 1149.7763 | 0 | 1196.2272 | 0 | 1244.5548 | 0 | 1294.8348 | 0 | 1347.1461 | 0 | 1401.5708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aerial Inspection | Preventive | Inspection | PV Module | 1 | 0 | 0 | N/A | MW | Inspector | 33.12 | 1 | 1 | Interval | 10 | 0 | 0 | 900 | 0 | 9000 | 9000 |  |  | 11152.4927 | 128101.336 | 6.042% | 9180 | 9363.6 | 9550.872 | 9741.8894 | 9936.7272 | 10135.4618 | 10338.171 | 10544.9344 | 10755.8331 | 10970.9498 | 11190.3688 | 11414.1762 | 11642.4597 | 11875.3089 | 12112.815 | 12355.0713 | 12602.1728 | 12854.2162 | 13111.3006 | 13373.5266 | 13640.9971 | 13913.817 | 14192.0934 | 14475.9352 | 14765.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128101.336 | 6.042% | 9180 | 9363.6 | 9550.872 | 9741.8894 | 9936.7272 | 10135.4618 | 10338.171 | 10544.9344 | 10755.8331 | 10970.9498 | 11190.3688 | 11414.1762 | 11642.4597 | 11875.3089 | 12112.815 | 12355.0713 | 12602.1728 | 12854.2162 | 13111.3006 | 13373.5266 | 13640.9971 | 13913.817 | 14192.0934 | 14475.9352 | 14765.454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Use infrared camera to inspect for hot spots; bypass diode failure | Preventive | Inspection | PV Module | 0 | 0 | 0 | N/A | strings | Inspector | 33.12 | 5 | 1 | interval | 2341.9204 | 0.15 | 70.2576 | 0 | 11634.6604 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test modules showing corrosion of ribbons to junction box | Preventive | Testing | PV Module | 0 | 0 | 0 | N/A | modules | Journeyman electrician | 19.9038 | 25 | 3 | Weibull | 32787 | 0.08 | 104.9184 | 0 | 52206.9923 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Test output of modules that exhibit cracked glass, bubble formation oxidation of busbars, discoloration of busbars, or PV module hot spots (bypass diode failure) | Preventive | Testing | PV Module | 0 | 0 | 0 | N/A | modules | Journeyman electrician | 19.9038 | 25 | 3 | Weibull | 32787 | 0.08 | 104.9184 | 0 | 52206.9923 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Roof inspection | Preventive | Inspection | Roof | 0 | 0 | 0 | N/A | m2 | Roofing | 22.7037 | 2 | 1 | Interval | 0 | 0.0075 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Remove leaves and debris from rack | Preventive | Service | Roof | 0 | 0 | 0 | N/A | m2 | Roofing | 22.7037 | 1 | 1 | Interval | 0 | 0.005 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check Electrical connections & enclosure for tracking motor/controller | Preventive | Inspection | Tracker | 0 | 0 | 0 | N/A | Controller | Inspector | 33.12 | 1 | 1 | interval | 16 | 0.083333 | 1.3333 | 0 | 44.16 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check Electrical connections (motor) | Preventive | Inspection | Tracker | 0 | 0 | 0 | N/A | Motor | Inspector | 33.12 | 1 | 1 | interval | 0 | 0.083333 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Check Grounding Braids for wear | Preventive | Inspection | Tracker | 1 | 0 | 0 | N/A | Structure | Inspector | 33.12 | 1 | 1 | interval | 327.8689 | 0.004 | 1.3115 | 0 | 43.4361 | 0 | 43.4361 |  |  | 53.8245 | 618.2464 | 0.02916% | 44.3048 | 45.1909 | 46.0947 | 47.0166 | 47.9569 | 48.9161 | 49.8944 | 50.8923 | 51.9101 | 52.9483 | 54.0073 | 55.0874 | 56.1892 | 57.313 | 58.4592 | 59.6284 | 60.821 | 62.0374 | 63.2781 | 64.5437 | 65.8346 | 67.1513 | 68.4943 | 69.8642 | 71.2615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 618.2464 | 0.02916% | 44.3048 | 45.1909 | 46.0947 | 47.0166 | 47.9569 | 48.9161 | 49.8944 | 50.8923 | 51.9101 | 52.9483 | 54.0073 | 55.0874 | 56.1892 | 57.313 | 58.4592 | 59.6284 | 60.821 | 62.0374 | 63.2781 | 64.5437 | 65.8346 | 67.1513 | 68.4943 | 69.8642 | 71.2615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Anemometer inspection | Preventive | Inspection | Tracker | 1 | 0 | 0 | N/A |  | Inspector | 33.12 | 1 | 1 | interval | 1 | 0.1 | 0.1 | 0 | 3.312 | 0 | 3.312 |  |  | 4.1041 | 47.1413 | 0.002223% | 3.3782 | 3.4458 | 3.5147 | 3.585 | 3.6567 | 3.7298 | 3.8044 | 3.8805 | 3.9581 | 4.0373 | 4.1181 | 4.2004 | 4.2844 | 4.3701 | 4.4575 | 4.5467 | 4.6376 | 4.7304 | 4.825 | 4.9215 | 5.0199 | 5.1203 | 5.2227 | 5.3271 | 5.4337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.1413 | 0.002223% | 3.3782 | 3.4458 | 3.5147 | 3.585 | 3.6567 | 3.7298 | 3.8044 | 3.8805 | 3.9581 | 4.0373 | 4.1181 | 4.2004 | 4.2844 | 4.3701 | 4.4575 | 4.5467 | 4.6376 | 4.7304 | 4.825 | 4.9215 | 5.0199 | 5.1203 | 5.2227 | 5.3271 | 5.4337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Driveshaft torque check & visual inspection | Preventive | Inspection | Tracker | 1 | 0 | 0 | N/A | Driveshaft | Inspector | 33.12 | 1 | 1 | interval | 307.377 | 0.0083333 | 2.5615 | 0 | 84.8361 | 0 | 84.8361 |  |  | 105.126 | 1207.5126 | 0.05695% | 86.5328 | 88.2634 | 90.0287 | 91.8293 | 93.6659 | 95.5392 | 97.45 | 99.399 | 101.387 | 103.4147 | 105.483 | 107.5926 | 109.7445 | 111.9394 | 114.1782 | 116.4617 | 118.791 | 121.1668 | 123.5901 | 126.0619 | 128.5832 | 131.1548 | 133.7779 | 136.4535 | 139.1826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1207.5126 | 0.05695% | 86.5328 | 88.2634 | 90.0287 | 91.8293 | 93.6659 | 95.5392 | 97.45 | 99.399 | 101.387 | 103.4147 | 105.483 | 107.5926 | 109.7445 | 111.9394 | 114.1782 | 116.4617 | 118.791 | 121.1668 | 123.5901 | 126.0619 | 128.5832 | 131.1548 | 133.7779 | 136.4535 | 139.1826 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gearbox lubrication | Preventive | Service | Tracker | 1 | 0 | 0 | N/A | block | Mechanic | 29.2985 | 0.5 | 1 | interval | 10.2459 | 0.25 | 5.123 | 0 | 75.0473 | 0 | 75.0473 |  |  | 185.9921 | 2136.3684 | 0.1008% | 153.0965 | 156.1584 | 159.2816 | 162.4672 | 165.7165 | 169.0309 | 172.4115 | 175.8597 | 179.3769 | 182.9645 | 186.6237 | 190.3562 | 194.1633 | 198.0466 | 202.0075 | 206.0477 | 210.1686 | 214.372 | 218.6595 | 223.0326 | 227.4933 | 232.0432 | 236.684 | 241.4177 | 246.2461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2136.3684 | 0.1008% | 153.0965 | 156.1584 | 159.2816 | 162.4672 | 165.7165 | 169.0309 | 172.4115 | 175.8597 | 179.3769 | 182.9645 | 186.6237 | 190.3562 | 194.1633 | 198.0466 | 202.0075 | 206.0477 | 210.1686 | 214.372 | 218.6595 | 223.0326 | 227.4933 | 232.0432 | 236.684 | 241.4177 | 246.2461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inclinometer inspection | Preventive | Inspection | Tracker | 1 | 0 | 0 | N/A |  | Inspector | 33.12 | 1 | 1 | interval | 1 | 0.1 | 0.1 | 0 | 3.312 | 0 | 3.312 |  |  | 4.1041 | 47.1413 | 0.002223% | 3.3782 | 3.4458 | 3.5147 | 3.585 | 3.6567 | 3.7298 | 3.8044 | 3.8805 | 3.9581 | 4.0373 | 4.1181 | 4.2004 | 4.2844 | 4.3701 | 4.4575 | 4.5467 | 4.6376 | 4.7304 | 4.825 | 4.9215 | 5.0199 | 5.1203 | 5.2227 | 5.3271 | 5.4337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.1413 | 0.002223% | 3.3782 | 3.4458 | 3.5147 | 3.585 | 3.6567 | 3.7298 | 3.8044 | 3.8805 | 3.9581 | 4.0373 | 4.1181 | 4.2004 | 4.2844 | 4.3701 | 4.4575 | 4.5467 | 4.6376 | 4.7304 | 4.825 | 4.9215 | 5.0199 | 5.1203 | 5.2227 | 5.3271 | 5.4337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Limit switch inspection | Preventive | Inspection | Tracker | 1 | 0 | 0 | N/A | block | Inspector | 33.12 | 1 | 1 | interval | 10.2459 | 0.1 | 1.0246 | 0 | 33.9344 | 0 | 33.9344 |  |  | 42.0504 | 483.005 | 0.02278% | 34.6131 | 35.3054 | 36.0115 | 36.7317 | 37.4663 | 38.2157 | 38.98 | 39.7596 | 40.5548 | 41.3659 | 42.1932 | 43.0371 | 43.8978 | 44.7758 | 45.6713 | 46.5847 | 47.5164 | 48.4667 | 49.4361 | 50.4248 | 51.4333 | 52.4619 | 53.5112 | 54.5814 | 55.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483.005 | 0.02278% | 34.6131 | 35.3054 | 36.0115 | 36.7317 | 37.4663 | 38.2157 | 38.98 | 39.7596 | 40.5548 | 41.3659 | 42.1932 | 43.0371 | 43.8978 | 44.7758 | 45.6713 | 46.5847 | 47.5164 | 48.4667 | 49.4361 | 50.4248 | 51.4333 | 52.4619 | 53.5112 | 54.5814 | 55.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Module table inspection | Preventive | Inspection | Tracker | 1 | 0 | 0 | N/A | connection | Inspector | 33.12 | 1 | 1 | interval | 1639.3443 | 0.1 | 163.9344 | 0 | 5429.5082 | 0 | 5429.5082 |  |  | 6728.0612 | 77280.806 | 3.645% | 5538.0984 | 5648.8603 | 5761.8375 | 5877.0743 | 5994.6158 | 6114.5081 | 6236.7982 | 6361.5342 | 6488.7649 | 6618.5402 | 6750.911 | 6885.9292 | 7023.6478 | 7164.1208 | 7307.4032 | 7453.5512 | 7602.6223 | 7754.6747 | 7909.7682 | 8067.9636 | 8229.3228 | 8393.9093 | 8561.7875 | 8733.0232 | 8907.6837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77280.806 | 3.645% | 5538.0984 | 5648.8603 | 5761.8375 | 5877.0743 | 5994.6158 | 6114.5081 | 6236.7982 | 6361.5342 | 6488.7649 | 6618.5402 | 6750.911 | 6885.9292 | 7023.6478 | 7164.1208 | 7307.4032 | 7453.5512 | 7602.6223 | 7754.6747 | 7909.7682 | 8067.9636 | 8229.3228 | 8393.9093 | 8561.7875 | 8733.0232 | 8907.6837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Screw jack greasing | Preventive | Service | Tracker | 1 | 0 | 0 | N/A | block | Mechanic | 29.2985 | 0.5 | 1 | interval | 10.2459 | 0.25 | 5.123 | 0 | 75.0473 | 0 | 75.0473 |  |  | 185.9921 | 2136.3684 | 0.1008% | 153.0965 | 156.1584 | 159.2816 | 162.4672 | 165.7165 | 169.0309 | 172.4115 | 175.8597 | 179.3769 | 182.9645 | 186.6237 | 190.3562 | 194.1633 | 198.0466 | 202.0075 | 206.0477 | 210.1686 | 214.372 | 218.6595 | 223.0326 | 227.4933 | 232.0432 | 236.684 | 241.4177 | 246.2461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2136.3684 | 0.1008% | 153.0965 | 156.1584 | 159.2816 | 162.4672 | 165.7165 | 169.0309 | 172.4115 | 175.8597 | 179.3769 | 182.9645 | 186.6237 | 190.3562 | 194.1633 | 198.0466 | 202.0075 | 206.0477 | 210.1686 | 214.372 | 218.6595 | 223.0326 | 227.4933 | 232.0432 | 236.684 | 241.4177 | 246.2461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Screw jack inspection | Preventive | Inspection | Tracker | 1 | 0 | 0 | N/A | block | Inspector | 33.12 | 0.5 | 1 | interval | 10.2459 | 0.1 | 2.0492 | 0 | 33.9344 | 0 | 33.9344 |  |  | 84.1008 | 966.0101 | 0.04556% | 69.2262 | 70.6108 | 72.023 | 73.4634 | 74.9327 | 76.4314 | 77.96 | 79.5192 | 81.1096 | 82.7318 | 84.3864 | 86.0741 | 87.7956 | 89.5515 | 91.3425 | 93.1694 | 95.0328 | 96.9334 | 98.8721 | 100.8495 | 102.8665 | 104.9239 | 107.0223 | 109.1628 | 111.346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 966.0101 | 0.04556% | 69.2262 | 70.6108 | 72.023 | 73.4634 | 74.9327 | 76.4314 | 77.96 | 79.5192 | 81.1096 | 82.7318 | 84.3864 | 86.0741 | 87.7956 | 89.5515 | 91.3425 | 93.1694 | 95.0328 | 96.9334 | 98.8721 | 100.8495 | 102.8665 | 104.9239 | 107.0223 | 109.1628 | 111.346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Slew gear lubrication | Preventive | Service | Tracker | 1 | 0 | 0 | N/A | Slew Gear | Mechanic | 29.2985 | 3 | 1 | interval | 0 | 0.25 | 0 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Slew gear torque check & wear inspection | Preventive | Inspection | Tracker | 1 | 0 | 0 | N/A | Slew Gear | Inspector | 33.12 | 1 | 1 | interval | 163.9344 | 0.016667 | 2.7322 | 0 | 90.4918 | 0 | 90.4918 |  |  | 112.1344 | 1288.0134 | 0.06075% | 92.3016 | 94.1477 | 96.0306 | 97.9512 | 99.9103 | 101.9085 | 103.9466 | 106.0256 | 108.1461 | 110.309 | 112.5152 | 114.7655 | 117.0608 | 119.402 | 121.7901 | 124.2259 | 126.7104 | 129.2446 | 131.8295 | 134.4661 | 137.1554 | 139.8985 | 142.6965 | 145.5504 | 148.4614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1288.0134 | 0.06075% | 92.3016 | 94.1477 | 96.0306 | 97.9512 | 99.9103 | 101.9085 | 103.9466 | 106.0256 | 108.1461 | 110.309 | 112.5152 | 114.7655 | 117.0608 | 119.402 | 121.7901 | 124.2259 | 126.7104 | 129.2446 | 131.8295 | 134.4661 | 137.1554 | 139.8985 | 142.6965 | 145.5504 | 148.4614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tracking Controller inspection | Preventive | Inspection | Tracker | 1 | 0 | 0 | N/A |  | Inspector | 33.12 | 1 | 1 | interval | 10.2459 | 0.1 | 1.0246 | 0 | 33.9344 | 0 | 33.9344 |  |  | 42.0504 | 483.005 | 0.02278% | 34.6131 | 35.3054 | 36.0115 | 36.7317 | 37.4663 | 38.2157 | 38.98 | 39.7596 | 40.5548 | 41.3659 | 42.1932 | 43.0371 | 43.8978 | 44.7758 | 45.6713 | 46.5847 | 47.5164 | 48.4667 | 49.4361 | 50.4248 | 51.4333 | 52.4619 | 53.5112 | 54.5814 | 55.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 483.005 | 0.02278% | 34.6131 | 35.3054 | 36.0115 | 36.7317 | 37.4663 | 38.2157 | 38.98 | 39.7596 | 40.5548 | 41.3659 | 42.1932 | 43.0371 | 43.8978 | 44.7758 | 45.6713 | 46.5847 | 47.5164 | 48.4667 | 49.4361 | 50.4248 | 51.4333 | 52.4619 | 53.5112 | 54.5814 | 55.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Universal joint greasing (zirc fitting) | Preventive | Service | Tracker | 0 | 0 | 0 | N/A | Driveshaft | Mechanic | 29.2985 | 0.5 | 1 | interval | 0 | 0.16667 | 0 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Universal joint inspection | Preventive | Inspection | Tracker | 0 | 0 | 0 | N/A | Driveshaft | Inspector | 33.12 | 1 | 1 | interval | 0 | 0.0083333 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lubricate tracker mounting bearings/gimbals | Preventive | Service | Tracker | 0 | 0 | 0 | N/A |  | Mechanic | 29.2985 | 1 | 1 | interval | 0 | 0.15 | 0 | 1 | 0 | 0 | 0 |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Inspect transformer meter, oil and tempertaure gauges | Preventive | Inspection | Transformer | 1 | 0 | 0 | N/A |  | Master electrician | 32.012 | 1 | 1 | interval | 10 | 0.25 | 2.5 | 0 | 80.03 | 0 | 80.03 |  |  | 99.1705 | 1139.1062 | 0.05373% | 81.6306 | 83.2633 | 84.9285 | 86.6271 | 88.3596 | 90.1268 | 91.9294 | 93.768 | 95.6433 | 97.5562 | 99.5073 | 101.4975 | 103.5274 | 105.5979 | 107.7099 | 109.8641 | 112.0614 | 114.3026 | 116.5887 | 118.9204 | 121.2989 | 123.7248 | 126.1993 | 128.7233 | 131.2978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1139.1062 | 0.05373% | 81.6306 | 83.2633 | 84.9285 | 86.6271 | 88.3596 | 90.1268 | 91.9294 | 93.768 | 95.6433 | 97.5562 | 99.5073 | 101.4975 | 103.5274 | 105.5979 | 107.7099 | 109.8641 | 112.0614 | 114.3026 | 116.5887 | 118.9204 | 121.2989 | 123.7248 | 126.1993 | 128.7233 | 131.2978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ANNUAL TOTAL | [22 empty] | 148619.7715 | 2120221.5634 | 1 | 60724.0436 | 92998.1339 | 93544.6629 | 96139.8825 | 126946.4684 | 100090.6021 | 101371.8554 | 104857.3277 | 106497.7843 | 143417.3473 | 178521.2288 | 180847.5842 | 181165.5114 | 183916.0108 | 223072.7762 | 187584.5878 | 188347.4407 | 191605.664 | 192395.8634 | 238350.6541 | 679236.268 | 685279.8739 | 685970.4451 | 686825.4451 | 729408.8354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3392628.7776 | 1.6001 | 61847.3281 | 155324.2267 | 150035.0964 | 146930.984 | 172198.2875 | 139985.5371 | 136113.0076 | 135394.4338 | 133363.7579 | 166933.8478 | 271410.4521 | 259362.4633 | 247672.6437 | 240485.5411 | 271424.9643 | 229333.8851 | 226749.2334 | 233371.2664 | 238230.6519 | 287264.2924 | 1519994.1092 | 1492795.7541 | 1444325.0772 | 1382804.7592 | 1351973.4208 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ANNUAL PRODUCTION | [25 empty] | 13949600 | 13899381.44 | 13849343.6668 | 13799486.0296 | 13749807.8799 | 13700308.5715 | 13650987.4607 | 13601843.9058 | 13552877.2678 | 13504086.9096 | 13455472.1967 | 13407032.4968 | 13358767.1798 | 13310675.618 | 13262757.1858 | 13215011.2599 | 13167437.2194 | 13120034.4454 | 13072802.3214 | 13025740.233 | 12978847.5682 | 12932123.7169 | 12885568.0715 | 12839180.0265 | 12792958.9784 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13 |  |  | 13949600 | 13899381.44 | 13849343.6668 | 13799486.0296 | 13749807.8799 | 13700308.5715 | 13650987.4607 | 13601843.9058 | 13552877.2678 | 13504086.9096 | 13455472.1967 | 13407032.4968 | 13358767.1798 | 13310675.618 | 13262757.1858 | 13215011.2599 | 13167437.2194 | 13120034.4454 | 13072802.3214 | 13025740.233 | 12978847.5682 | 12932123.7169 | 12885568.0715 | 12839180.0265 | 12792958.9784 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13 | 1e-13
Annual Average $/kWh/year | [25 empty] | 0.0043531 | 0.0066908 | 0.0067544 | 0.0069669 | 0.0092326 | 0.0073057 | 0.007426 | 0.0077091 | 0.0078579 | 0.01062 | 0.013268 | 0.013489 | 0.013562 | 0.013817 | 0.016819 | 0.014195 | 0.014304 | 0.014604 | 0.014717 | 0.018298 | 0.052334 | 0.052991 | 0.053236 | 0.053494 | 0.057016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0.0044336 | 0.011175 | 0.010833 | 0.010648 | 0.012524 | 0.010218 | 0.0099709 | 0.0099541 | 0.0098403 | 0.012362 | 0.020171 | 0.019345 | 0.01854 | 0.018067 | 0.020465 | 0.017354 | 0.01722 | 0.017787 | 0.018223 | 0.022054 | 0.11711 | 0.11543 | 0.11209 | 0.1077 | 0.10568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2120221.5634

## Labor Rates
Service Provider |  | Overhead Mulitpier | Rate ($/hour) | Labor Multiplier (fully loaded) | Loaded Rate ($/hour) | Scope of Work | Salary (2080 hrs/year) | Qualifications
Administrator | 22.9956 | 1.38 | 16.6635 | 1.38 | 22.9956 | Record-keeping, service confirmation, correspondence | 47830.8 | Excellent interpersonal and communication skills (written and verbal). Diligent record keeping. 2 to 5 years of experience. Excellent MS Office and computer skills. Management of contractors and quality.
Cleaner | 14.7355 | 1.38 | 10.6779 | 1.38 | 14.7355 | Cleaning PV Arrays | 30649.8 | 10 OSHA Card; Required level of bonding and insurance; drivers license and reliable transportation; minimum 18 years old.
Designer | 58.3315 | 1.38 | 42.2692 | 1.38 | 58.3315 | Specifications, drawings, modeling and analysis, codes and standards. | 121329.6 | B.S. in EE (4-year engineering degree); registered PE licensed to practice engineering in the jurisdiction; NABCEP PV Installer Certification; CAD (AutoCAD) and graphics skills; knowledge of IEEE, NEC, NESC, and other codes and standards for PV systems; required level of errors and omissions insurance.
Inspector | 33.12 | 1.38 | 24 | 1.38 | 33.12 | Diagnostic analysis; visual inspection, specific testing, | 68889.6 | Diagnostic analysis; NABCEP PV Installer Certification; 2 to 5 years of experience.
Inverter specialist | 33.1731 | 1.38 | 24.0385 | 1.38 | 33.1731 | Inverter repair, upgrades | 69000 | (estimated) Skills to perform maintenance, diagnostics and repair for inverter: factory trained and certified; 5+ years experience.
Journeyman electrician | 19.9038 | 1.38 | 14.4231 | 1.38 | 19.9038 | Module replacement, Inverter replacement, fuse/breaker replacement, conduit routing, wiring, ground fault repair | 41400 | (estimated) 50 OSHA Card; training in arc-flash, lock-out/tag-out, and other special protective equipment and procedures; NABCEP PV Installer certification; experience in the design of medium voltage electrical systems. 5+ years experience with PV systems; color vision.
Master electrician | 32.012 | 1.38 | 23.1971 | 1.38 | 32.012 | Module replacement, inverter replacement, fuse/breaker replacement, conduit routing, wiring, ground fault repair | 66585 | Electrical Contractor’s license for the jurisdictions; 50 OSHA Card; NABCEP PV Installer certification; experience in the design of medium voltage electrical systems. 5+ years experience with PV systems; color vision. Certification by the North American Energy Reliability Corporation (NERC) is necessary for positions that affect the power grid.
Mechanic | 29.2985 | 1.38 | 21.2308 | 1.38 | 29.2985 | Maintenance and repair/replace of tracking mount components | 60940.8 | 50 OSHA Card; 2 to 5 years of experience; required level of bonding and insurance.
Network/IT | 45.885 | 1.38 | 33.25 | 1.38 | 45.885 | Internet/network repair, monitoring equipment repair | 95440.8 | Knowledge of specific monitoring devices (training by system supplier) and how monitoring system is connected through network connections or wireless or cellular modem; knowledge of Modbus, DNP3 and other protocols, HMI operator interfaces; 2 to 5 years of experience. Locus, Enphase, Itron, etc. monitoring device knowledge.
Pest control | 20.1294 | 1.38 | 14.5865 | 1.38 | 20.1294 | Nesting vermin removal, Nesting vermin prevention | 41869.2 | 10 OSHA Card; safety training in handling animals and detritus; required level of bonding and insurance; drivers license and reliable transportation; minimum 18 years old; most states require license for pesticide
PV module/array Specialist | 33.1731 | 1.38 | 24.0385 | 1.38 | 33.1731 | Module repair | 69000 | (estimated) Skills to operate, troubleshoot, maintain, and repair photovoltaic equipment: NABCEP PV Installer certification. 2 to 5 years of experience.
Roofing | 22.7037 | 1.38 | 16.4519 | 1.38 | 22.7037 | Roof leak repair, roof tile repair, re-roof | 47223.6 | Roofing contractor’s license for the jurisdiction; 10 OSHA Card; safety training in fall protection equipment and use (or 50 OSHA Card); required level of bonding and insurance
Structural engineer | 55.8237 | 1.38 | 40.4519 | 1.38 | 55.8237 | Foundations and rack inspection/design | 116113.2 | B.S. CE (4-year engineering degree); registered PE licensed to practice engineering in the jurisdiction.
Mower/Trimmer | 15.7506 | 1.38 | 11.4135 | 1.38 | 15.7506 | Removal of vegetation | 32761.2 | 50 OSHA Card; drivers license and reliable transportation; required level of insurance; minimum 18 years old; any required training or license for herbicide application.
Utilities locator | 25.5499 | 1.38 | 18.5144 | 1.38 | 25.5499 | Locate underground utilities. | 53143.8 | 2 to5 years of experience.
Natinonal Bureau of Labor Statistics http://www.bls.gov/data/#wages

## Lists
O&M Type | Service Category | O&M Category | PV Module Type | Degradation rate per year | Module Encapsulant | Mounting Location | PV Sector | Environmental Conditions | Failure Distributions | Inverter Types | Replacemet Cost ($//W) | Warranty Types | Years | Roof Type | Repair Materials ($/m2) | Repair Labor (hours/m2) | Roof Slope | Rooftop Rack Type | Tracking | Inspection
Administration | Cleaning | AC Wiring | Amorphous silicon:0.87%/year | 0.0087 | Ethyl Vinyl Acetate (EVA) | Rooftop | All | Snow | Interval | String Inverter | 0.3 | EPC | 1 | Thermoplastic Polyolefin (TPO) | 20 | 1 | Flat or less than 1:12 | Ballasted | Fixed Tilt | Arial
Design | Emergency Response | DC Wiring | Mono-crystal silicon: 0.36%/year | 0.0036 | Polyvinyl Butyral (PVB) | Ground Mount | Residential (10 kW) | Humid | Weibull | Central Inverter | 0.19 | Inverter | 10 | Ethylene Propylene Diene Monomer (EPDM) | 20 | 1 | Sloped, 4:12 | Attached | 1-axis Tracking | Roof Walk
Preventive | Inspection | Asset Management | Mulit-crystal Silicon:0.64%/year | 0.0064 | Silicone |  | Commercial (1000 kW) | Hot (reduce efficiency 2.67% for central, 0.18% for string inverter, Wang et al 2012) | Log normal | Microinverter | 0.51 | Module (Product) | 20 | PolyVinyl Cloride (PVC) | 20 | 1 | Steep, more than 7/12 | Both ballasted and attached | 2-axis Tracking | Ground Walk
Corrective | Management | Documents | Cadmium telluride: 0.40%/year | 0.004 |  |  | Utility (1 MW) | Pollen |  |  |  | Monitoring | 0 | Built-up, Bituminous | 15 | 1.5
Decommission | Service | Electrical | CIGS:0.96%/year | 0.0096 |  |  |  | High Wind |  |  |  | N/A | 0 | Styrene-Butadiene-Styrene (SBS) | 20 | 1
| Testing | Mechanical | Concentrator | 0.01 |  |  |  | Hail | [5 empty] | Ashphalt Shingle | 15 | 1
| Repair | Inverter | Photovoltaic Degradation Rates — An Analytical Review Dirk C. Jordan and Sarah R. Kurtz; http://www.nrel.gov/docs/fy12osti/51664.pdf |  |  |  |  | Salt Air | [5 empty] | Composite Shingle | 25 | 1
|  | Meter | [5 empty] | Diesel Soot (reduce efficiency 1%/g, Wang et al 2012) | [5 empty] | Wood Shingle | 40 | 2
|  | Monitoring | [5 empty] | Industrial Emissions (reduce efficiency 1%/g, Wang et al 2012) | [5 empty] | Slate | 50 | 1
|  | Roof | [5 empty] | Bird Populations | [5 empty] | Metal Roof | 50 | 0.5
|  | Rack | [5 empty] | Construction Site Nearby (reduce efficiency 1%/g, Wang et al 2012) | [5 empty] | Tile | 50 | 1
|  | PV Module | [5 empty] | Sand/Dust (reduce efficiency 1%/g, Wang et al 2012) | [5 empty] | http://welcome.homeadvisor.com/costguide_roofing and http://www.homeadvisor.com/cost/roofing/repair-a-roof/] [
|  | Tracker | [5 empty] | High Insolation (reduce availability 0.83%, Wang et al 2012)
Transformer
Whole System

## Instructions
This model was developed as a collaboration between the SunSpec Alliance and The National Renewable Energy Laboratory
PVOMcost Proforma; a proforma cost modelling tool for PV industry operations and finance practitioners designing and budgetting PV O&M plans
Contents | Type | Description
Inputs & Summary | User inputs | Primary input page with real-time model output. Select system type, enter basic system details, warranty switches for modelling service plans, etc. here
Commercial Rooftop Details | User inputs | [Optional] Modify detailed assumptions for Commercial Rooftop system type. Exercise caution when modifying default assumptions.
Residential Rooftop Details | User inputs | [Optional] Modify detailed assumptions for Residential Rooftop system type. Exercise caution when modifying default assumptions.
Ground-Mount Details | User inputs | [Optional] Modify detailed assumptions for Ground-Mount system type. Exercise caution when modifying default assumptions.
Labor Rates | User inputs | [Optional] Modify labor rate assumptions for each trade
Reports | Read-only | Additional model output summaries; read-only
Cash Flow | Read-only | Detailed line item cash flow output; read-only
Cleaning | Separate tool | Stand-alone modelling tool provided to help calculate optimal PV panel cleaning frequency. Not connected to model; must manully transfer result to appropriate details page
Legend
User input, hard-coded default value |  | Value
User input, calculated default value |  | Value
User input, drop down selection |  | Value
Input not applicable (user can over ride) |  | Value
Read-only output |  | Value
Note: Model is for informational purposes only
Please direct any comments for improvements or feedback to support@sunspec.org; This tool is provided in an open source format, please send improvements and derivative models to PVOMcostModel@sunspec.org
LICENSE AGREEMENT
THIS DOCUMENT AND THE INFORMATION CONTAINED HEREIN IS PROVIDED ON AN "AS IS" BASIS. THE SUNSPEC ALLIANCE DISCLAIMS ALL WARRANTIES,
EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY WARRANTY THAT THE USE OF THE INFORMATION HEREIN WILL NOT INFRINGE ANY OWNERSHIP
RIGHTS OR ANY IMPLIED WARRANTIES OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE.
THIS DOCUMENT MAY BE USED, COPIED, AND FURNISHED TO OTHERS, WITHOUT RESTRICTIONS OF ANY KIND, PROVIDED THAT THIS DOCUMENT ITSELF MAY NOT
BE MODIFIED IN ANYWAY, EXCEPT AS NEEDED BY THE SUNSPEC TECHNICAL COMMITTEE AND AS GOVERNED BY THE SUNSPEC IPR POLICY.
THE COMPLETE POLICY OF THE SUNSPEC ALLIANCE CAN BE FOUND AT WWW.SUNSPEC.ORG.